Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830


         985-649-5832

Slidell, LA 70458



Slidell, LA  70459

FAX 985-641-5950

Ashford Place

Monroe, Louisiana

Date of Inspection:  October 17, 2006

Unit 8 and 10

GENERAL:

1) Spray a mold remediation solution on all wood that was stored outside prior to building the structure.  This must be completed before applying sheet-rock.

2) Install nail guards on top and bottom, front and back at all electrical panels as required.

3) Strapping must be used on all plumbing lines when placed inside walls, especially at bathtubs, washing machines and hot water heaters.

4) Fire caulk all plumbing when penetrating a rated structure.  

5) It was noted that several outlet boxes on common walls/ceilings were closer than the manufactures specifications called for.  All outlet boxes, electrical, cable, telephone, or security, that are used on a shared wall or ceilings between apartments, fire partitions, must meet the following:

a. Clearance between boxes and cutouts in wall, sheetrock, shall not exceed 1/8 in.

b. The area of openings in the sheetrock for boxes shall not aggregate more than 100 sq in. per 100 sq ft of wall or partition area with no opening exceeding 22.0 sq. in.

c. Outlet boxes on opposite sides of wall or partition shall be separated by a horizontal distance of not less than 24 in.
6) Exhaust vents in the restrooms have been moved from the ceiling to the wall.  These vent hoses must have nail guards on both sides of the header board when penetration is made.  The hose is 3” and the header is only 3-1/2”. 

7) All HVAC flex hoses must be supported by straps.  It was noted in several places that the sprinkler system piping was supporting the HVAC flex hose.

Building 8 was complete except for sheetrock.  All of the items listed in the General section were noted in building 8.  Local rains flooded the first floor, approximately 6 inches of water stayed long enough to make a watermark.  The entire first floor must have the mud removed and the studs and base plates must be dried before sheetrock can be applied.  All installed insulation must be replaced.  Landscaping must be completed to ensure the first floor does not flood again.  Because of the floodwater it appears that the non-corrugated nail guard plates have rusted.  These nail guard plates need to be replaced prior to sheetrocking.  One flexible HVAC duct on the second floor was routed 180 degrees in a very short amount of space.  Excessive bends in HVAC ducts will not allow for proper airflow.  A dryer vent hose improperly installed and is damaged.   

Building 10 was complete except for sheetrock.  One exhaust fan hose for a restroom was broken and needs to be repaired prior to sheetrocking.

David Dammon

Dammon Engineering

