Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
09/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260526 - GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

NFPA 70 and IEEE C2 include basic grounding requirements for electrical safety.  This Section supplements those requirements with additional grounding and with optional grounding methods and materials for both power and electronic systems that go beyond basic minimum safety requirements.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes methods and materials for grounding systems and equipment[.][, plus the following special applications:]

Retain optional text in paragraph above with one or more subparagraphs below for special grounding applications.  Delete subparagraphs if deleting optional text.

1. Overhead-lines grounding.

2. Underground distribution grounding.

3. Common ground bonding with lightning protection system.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.

Retain paragraph and subparagraphs below to require that Contractor provide drawings to locate significant grounding features.  Division 01 Sections "Project Record Documents" and "Operation and Maintenance Data" require submittals to be included in those documents for use by maintenance forces throughout the life of the Project.

B. Other Informational Submittals:  Plans showing dimensioned as-built locations of grounding features specified in Part 3 "Field Quality Control" Article, including the following:

1. Test wells.

2. Ground rods.

3. Ground rings.

4. Grounding arrangements and connections for separately derived systems.

5. Grounding for sensitive electronic equipment.

6. <Insert items.>

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For testing agency and testing agency's field supervisor.

Retain paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

Retain paragraph and subparagraphs below if Section specifies test wells, separately derived systems, or ground ring or other grounding for sensitive electronic equipment.

E. Operation and Maintenance Data:  For grounding to include the following in emergency, operation, and maintenance manuals:

Retain and edit subparagraph and associated subparagraphs below for projects requiring a high reliability for electrical systems.  NETA MTS provides more easily interpreted recommendations for frequency of tests and inspections than NFPA 70B.

1. Instructions for periodic testing and inspection of grounding features at [test wells] [ground rings] [grounding connections for separately derived systems] <Insert locations> based on [NETA MTS] [NFPA 70B] <Insert reference>.

a. Tests shall be to determine if ground resistance or impedance values remain within specified maximums, and instructions shall recommend corrective action if they do not.

b. Include recommended testing intervals.

1.4 QUALITY ASSURANCE

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and it lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association to supervise on-site testing specified in Part 3.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with UL 467 for grounding and bonding materials and equipment.

PART 2 -  PRODUCTS

2.1 CONDUCTORS

Retain first paragraph below to require one of the two preferred conductor materials permitted by NFPA 70; or delete to allow Contractor to select any material that complies with Code.  See "Product Characteristics" Article in the Evaluations for discussion on alternative materials.

A. Insulated Conductors:  [Copper] [or] [tinned-copper] wire or cable insulated for 600 V unless otherwise required by applicable Code or authorities having jurisdiction.

B. Bare Copper Conductors:

1. Solid Conductors:  ASTM B 3.

2. Stranded Conductors:  ASTM B 8.

3. Tinned Conductors:  ASTM B 33.

Sizes and types of conductors in four subparagraphs below are typical examples.  28-kcmil bonding cable in first subparagraph below is slightly larger than No. 6 AWG.

4. Bonding Cable:  28 kcmil, 14 strands of No. 17 AWG conductor, 1/4 inch (6 mm) in diameter.

5. Bonding Conductor:  No. 4 or No. 6 AWG, stranded conductor.

6. Bonding Jumper:  Copper tape, braided conductors, terminated with copper ferrules; 1-5/8 inches (41 mm) wide and 1/16 inch (1.6 mm) thick.

7. Tinned Bonding Jumper:  Tinned-copper tape, braided conductors, terminated with copper ferrules; 1-5/8 inches (41 mm) wide and 1/16 inch (1.6 mm) thick.

Retain first paragraph and subparagraphs below if Project includes overhead-line work.

C. Bare Grounding Conductor and Conductor Protector for Wood Poles:

1. No. 4 AWG minimum, soft-drawn copper.

2. Conductor Protector:  Half-round PVC or wood molding.  If wood, use pressure-treated fir or cypress or cedar.

D. Grounding Bus:  Rectangular bars of annealed copper, [1/4 by 2 inches (6 by 50 mm)] <Insert dimensions> in cross section, unless otherwise indicated; with insulators.

2.2 CONNECTORS

A. Listed and labeled by a nationally recognized testing laboratory acceptable to authorities having jurisdiction for applications in which used, and for specific types, sizes, and combinations of conductors and other items connected.

B. Bolted Connectors for Conductors and Pipes:  Copper or copper alloy, bolted pressure-type, with at least two bolts.

1. Pipe Connectors:  Clamp type, sized for pipe.

C. Welded Connectors:  Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

2.3 GROUNDING ELECTRODES

NFPA 70 allows alternative types of grounding electrodes including ground rods, ground rings, metal underground water pipes, metal building frames, Ufer grounds, and pipe and plate electrodes.  Retain Part 3 "Applications" and "Installation" articles to specify where these items are required and coordinate with Drawings.

Copper-clad steel ground rods are most common grounding electrode.  See Evaluations for discussion on alternative materials.  Sectional rods are used when electrodes longer than 10 feet (3 m) are required.

A. Ground Rods:  [Copper-clad] [Zinc-coated] [Stainless] steel[, sectional type]; [3/4 inch by10 feet (19 mm by 3 m)] [5/8 by 96 inches (16 by 2400 mm)] in diameter.

Retain paragraph and subparagraphs below if allowed by authorities having jurisdiction to enhance grounding performance.  See Evaluations.

B. Chemical-Enhanced Grounding Electrodes:  Copper tube, straight or L-shaped, charged with [nonhazardous electrolytic chemical salts] <Insert enhancement material>.

1. Termination:  Factory-attached No. 4/0 AWG bare conductor at least 48 inches (1200 mm) long.

2. Backfill Material:  Electrode manufacturer's recommended material.

PART 3 -  EXECUTION

3.1 APPLICATIONS

A. Conductors:  Install solid conductor for No. [8] <Insert size> AWG and smaller, and stranded conductors for No. [6] <Insert size> AWG and larger, unless otherwise indicated.

Coordinate first paragraph and subparagraph below with Division 26 Section "Underground Ducts and Raceways for Electrical Systems" and with Drawings.

B. Underground Grounding Conductors:  Install bare [tinned-]copper conductor, No. [2/0] <Insert size> AWG minimum.

1. Bury at least 24 inches (600 mm) below grade.

Retain subparagraph below to require duct-bank grounding conductor to be installed with, but external to, duct bank.

2. Duct-Bank Grounding Conductor:  Bury 12 inches (300 mm) above duct bank when indicated as part of duct-bank installation.

C. Isolated Grounding Conductors:  Green-colored insulation with continuous yellow stripe.  On feeders with isolated ground, identify grounding conductor where visible to normal inspection, with alternating bands of green and yellow tape, with at least three bands of green and two bands of yellow.

Retain and edit first paragraph and subparagraphs below if grounding bus is required.  Coordinate with Drawings.

D. Grounding Bus:  Install in electrical and telephone equipment rooms, in rooms housing service equipment, and elsewhere as indicated.

1. Install bus on insulated spacers 1 inch (25 mm), minimum, from wall 6 inches (150 mm) above finished floor, unless otherwise indicated.

2. Where indicated on both sides of doorways, route bus up to top of door frame, across top of doorway, down to specified height above floor, and connect to horizontal bus.

E. Conductor Terminations and Connections:

1. Pipe and Equipment Grounding Conductor Terminations:  Bolted connectors.

2. Underground Connections:  Welded connectors, except at test wells and as otherwise indicated.

3. Connections to Ground Rods at Test Wells:  Bolted connectors.

4. Connections to Structural Steel:  Welded connectors.

3.2 GROUNDING OVERHEAD LINES

A. Comply with IEEE C2 grounding requirements.

Grounding practices of local utility company may differ from requirements in six paragraphs below.  Although overhead-line grounding specified in this Article is not for utility company's use and does not have to meet its standards, it is possible utility may be requested to repair or maintain the line in future.  For this reason, it may be desirable to design some grounding features according to its standards.  Utility companies, for economic reasons, often design to a standard lower than is appropriate for Project requirements.  Alternatively, because of their detailed experience with wind, ice, and lightning conditions in their service area, utility companies may design to a higher standard than is required by Code.  In addition to Project requirements, evaluate local utility company's practice and edit paragraphs accordingly.  This evaluation is particularly important if Project overhead lines connect with utility lines.  Coordinate with Drawings and with Division 26 Section "Low-Voltage Overhead Electrical Power Systems."

B. Install [2] <Insert number> parallel ground rods if resistance to ground by a single, ground-rod electrode exceeds 25 ohms.

C. Drive ground rods until tops are 12 inches (300 mm) below finished grade in undisturbed earth.

D. Ground-Rod Connections:  Install bolted connectors for underground connections and connections to rods.

E. Lightning Arrester Grounding Conductors:  Separate from other grounding conductors.

F. Secondary Neutral and Transformer Enclosure:  Interconnect and connect to grounding conductor.

G. Protect grounding conductors running on surface of wood poles with molding extended from grade level up to and through communication service and transformer spaces.

3.3 GROUNDING UNDERGROUND DISTRIBUTION SYSTEM COMPONENTS

A. Comply with IEEE C2 grounding requirements.

Grounding practices of local utility company may differ from requirements in three paragraphs below.  Although grounding specified in this Article is not for utility company's use and does not have to meet its standards, it is possible utility may be requested to repair or maintain the line in future.  For this reason, it may be desirable to design some grounding features according to its standards.  Utility companies, for economic reasons, often design to a standard lower than is appropriate for Project requirements.  Alternatively, because of their detailed experience with conditions in their service area, utility companies may design to a higher standard than is required by Code.  In addition to Project requirements, evaluate local utility company's practices and edit paragraphs accordingly.  This evaluation is particularly important if Project underground lines connect with utility lines.  Coordinate with Drawings and with Division 26 Section "Underground Ducts and Raceways for Electrical Systems.".

B. Grounding Manholes and Handholes:  Install a driven ground rod through manhole or handhole floor, close to wall, and set rod depth so 4 inches (100 mm) will extend above finished floor.  If necessary, install ground rod before manhole is placed and provide No. 1/0 AWG bare, tinned-copper conductor from ground rod into manhole through a waterproof sleeve in manhole wall.  Protect ground rods passing through concrete floor with a double wrapping of pressure-sensitive insulating tape or heat-shrunk insulating sleeve from 2 inches (50 mm) above to 6 inches (150 mm) below concrete.  Seal floor opening with waterproof, nonshrink grout.

C. Grounding Connections to Manhole Components:  Bond exposed-metal parts such as inserts, cable racks, pulling irons, ladders, and cable shields within each manhole or handhole, to ground rod or grounding conductor.  Make connections with No. 4 AWG minimum, stranded, hard-drawn copper bonding conductor.  Train conductors level or plumb around corners and fasten to manhole walls.  Connect to cable armor and cable shields as recommended by manufacturer of splicing and termination kits.

Retain and edit paragraph below to exceed NFPA 70 requirements.  If concrete pad is for equipment to be supplied by utility company, revise to comply with utility company's grounding standards or delete and detail on Drawings.

D. Pad-Mounted Transformers and Switches:  Install two ground rods and ground ring around the pad.  Ground pad-mounted equipment and noncurrent-carrying metal items associated with substations by connecting them to underground cable and grounding electrodes.  Install tinned-copper conductor not less than No. 2 AWG for ground ring and for taps to equipment grounding terminals.  Bury ground ring not less than 6 inches (150 mm) from the foundation.

3.4 EQUIPMENT GROUNDING

NFPA 70 permits or specifies two types of equipment grounding conductors:  metallic raceway or cable sheath that encloses supply conductors, and a separate grounding conductor of insulated wire or cable installed with supply conductors.  Installation of a separate insulated equipment grounding conductor provides an additional degree of safe operation when compared to relying on raceway or cable sheath for ground continuity.  NFPA 70 requires separate insulated equipment grounding conductors in some situations and not in others.  Retain and edit one of first two paragraphs below to require insulated equipment grounding conductors, which exceed NFPA 70 requirements.  Coordinate with Drawings.

A. Install insulated equipment grounding conductors with all feeders and branch circuits.

B. Install insulated equipment grounding conductors with the following items, in addition to those required by NFPA 70:

Retain applicable subparagraphs below.

1. Feeders and branch circuits.

2. Lighting circuits.

3. Receptacle circuits.

4. Single-phase motor and appliance branch circuits.

5. Three-phase motor and appliance branch circuits.

6. Flexible raceway runs.

7. Armored and metal-clad cable runs.

8. Busway Supply Circuits:  Install insulated equipment grounding conductor from grounding bus in the switchgear, switchboard, or distribution panel to equipment grounding bar terminal on busway.

9. Computer and Rack-Mounted Electronic Equipment Circuits:  Install insulated equipment grounding conductor in branch-circuit runs from equipment-area power panels and power-distribution units.

10. X-Ray Equipment Circuits:  Install insulated equipment grounding conductor in circuits supplying x-ray equipment.

C. Air-Duct Equipment Circuits:  Install insulated equipment grounding conductor to duct-mounted electrical devices operating at 120 V and more, including air cleaners, heaters, dampers, humidifiers, and other duct electrical equipment.  Bond conductor to each unit and to air duct and connected metallic piping.

D. Water Heater, Heat-Tracing, and Antifrost Heating Cables:  Install a separate insulated equipment grounding conductor to each electric water heater and heat-tracing cable.  Bond conductor to heater units, piping, connected equipment, and components.

E. Isolated Grounding Receptacle Circuits:  Install an insulated equipment grounding conductor connected to the receptacle grounding terminal.  Isolate conductor from raceway and from panelboard grounding terminals.  Terminate at equipment grounding conductor terminal of the applicable derived system or service, unless otherwise indicated.

F. Isolated Equipment Enclosure Circuits:  For designated equipment supplied by a branch circuit or feeder, isolate equipment enclosure from supply circuit raceway with a nonmetallic raceway fitting listed for the purpose.  Install fitting where raceway enters enclosure, and install a separate insulated equipment grounding conductor.  Isolate conductor from raceway and from panelboard grounding terminals.  Terminate at equipment grounding conductor terminal of the applicable derived system or service, unless otherwise indicated.

Coordinate paragraph and subparagraphs below with Drawings and Sections for signal and communication equipment.  Edit to suit Project.

G. Signal and Communication Equipment:  For telephone, alarm, voice and data, and other communication equipment, provide No. 4 AWG minimum insulated grounding conductor in raceway from grounding electrode system to each service location, terminal cabinet, wiring closet, and central equipment location.

1. Service and Central Equipment Locations and Wiring Closets:  Terminate grounding conductor on a 1/4-by-2-by-12-inch (6-by-50-by-300-mm) grounding bus.

2. Terminal Cabinets:  Terminate grounding conductor on cabinet grounding terminal.

Paragraph below may supplement equipment grounding conductor and may be in excess of NFPA 70 requirements.  Retain if necessary or desired and coordinate with Drawings.

H. [Metal] [and] [Wood] Poles Supporting Outdoor Lighting Fixtures:  Install grounding electrode and a separate insulated equipment grounding conductor in addition to grounding conductor installed with branch-circuit conductors.

3.5 INSTALLATION

A. Grounding Conductors:  Route along shortest and straightest paths possible, unless otherwise indicated or required by Code.  Avoid obstructing access or placing conductors where they may be subjected to strain, impact, or damage.

B. Common Ground Bonding with Lightning Protection System:  Comply with NFPA 780 and UL 96 when interconnecting with lightning protection system.  Bond electrical power system ground directly to lightning protection system grounding conductor at closest point to electrical service grounding electrode.  Use bonding conductor sized same as system grounding electrode conductor, and install in conduit.

C. Ground Rods:  Drive rods until tops are 2 inches (50 mm) below finished floor or final grade, unless otherwise indicated.

1. Interconnect ground rods with grounding electrode conductor below grade and as otherwise indicated.  Make connections without exposing steel or damaging coating, if any.

Delete subparagraph below if grounding installation requirements are detailed on Drawings.  Subparagraph exceeds NFPA 70 requirements.

2. For grounding electrode system, install at least [three] <Insert number> rods spaced at least one-rod length from each other and located at least the same distance from other grounding electrodes, and connect to the service grounding electrode conductor.

Retain first paragraph and subparagraph below to require test wells; delete if detailed on Drawings.

D. Test Wells:  Ground rod driven through drilled hole in bottom of handhole.  Handholes are specified in Division 26 Section "Underground Ducts and Raceways for Electrical Systems," and shall be at least 12 inches (300 mm) deep, with cover.

1. Test Wells:  Install at least one test well for each service, unless otherwise indicated.  Install at the ground rod electrically closest to service entrance.  Set top of test well flush with finished grade or floor.

E. Bonding Straps and Jumpers:  Install in locations accessible for inspection and maintenance, except where routed through short lengths of conduit.

1. Bonding to Structure:  Bond straps directly to basic structure, taking care not to penetrate any adjacent parts.

2. Bonding to Equipment Mounted on Vibration Isolation Hangers and Supports:  Install so vibration is not transmitted to rigidly mounted equipment.

3. Use exothermic-welded connectors for outdoor locations, but if a disconnect-type connection is required, use a bolted clamp.

If connections specified in paragraph and subparagraphs below circumvent dielectric fittings intended to isolate interior piping systems from ground, other action may be necessary to prevent electrolytic corrosion.

F. Grounding and Bonding for Piping:

1. Metal Water Service Pipe:  Install insulated copper grounding conductors, in conduit, from building's main service equipment, or grounding bus, to main metal water service entrances to building.  Connect grounding conductors to main metal water service pipes, using a bolted clamp connector or by bolting a lug-type connector to a pipe flange, using one of the lug bolts of the flange.  Where a dielectric main water fitting is installed, connect grounding conductor on street side of fitting.  Bond metal grounding conductor conduit or sleeve to conductor at each end.

2. Water Meter Piping:  Use braided-type bonding jumpers to electrically bypass water meters.  Connect to pipe with a bolted connector.

3. Bond each aboveground portion of gas piping system downstream from equipment shutoff valve.

Retain and edit first paragraph below to exceed NFPA 70 requirements, and comply with NFPA 70 recommendations for a higher standard of safety or electromagnetic interference suppression if needed.

G. Bonding Interior Metal Ducts:  Bond metal air ducts to equipment grounding conductors of associated fans, blowers, electric heaters, and air cleaners.  Install [tinned ]bonding jumper to bond across flexible duct connections to achieve continuity.

H. Grounding for Steel Building Structure:  Install a driven ground rod at base of each corner column and at intermediate exterior columns at distances not more than 60 feet (18 m) apart.

See Evaluations for discussion on ground rings.

I. Ground Ring:  Install a grounding conductor, electrically connected to each building structure ground rod and to each [steel column] [indicated item], extending around the perimeter of [building] [area or item indicated].

1. Install tinned-copper conductor not less than No. [2/0] <Insert size> AWG for ground ring and for taps to building steel.

2. Bury ground ring not less than [24 inches (600 mm)] <Insert dimension> from building foundation.

Retain paragraph and subparagraphs below to require Ufer ground (concrete-encased grounding electrode).  20 feet (6 m) is minimum length of conductor for this item.  Coordinate with Drawings.  See Evaluations.

J. Ufer Ground (Concrete-Encased Grounding Electrode):  Fabricate according to NFPA 70, using a minimum of [20 feet (6 m)] <Insert length> of bare copper conductor not smaller than No. [4] <Insert size> AWG.

1. If concrete foundation is less than [20 feet (6 m)] <Insert dimension> long, coil excess conductor within base of foundation.

2. Bond grounding conductor to reinforcing steel in at least four locations and to anchor bolts.  Extend grounding conductor below grade and connect to building grounding grid or to grounding electrode external to concrete.

3.6 FIELD QUALITY CONTROL

Retain one of three paragraphs below.  Coordinate with "Quality Assurance" Article in Part 1.

A. Testing Agency:  Owner will engage a qualified testing and inspecting agency to perform field tests and inspections and prepare test reports.

B. Testing Agency:  Engage a qualified testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

C. Perform the following tests and inspections and prepare test reports:

Retain subparagraphs and associated subparagraphs below with either of last two paragraphs above.  Edit to suit Project.  Delete if testing will be performed by Owner-engaged testing and inspecting agency.

1. After installing grounding system but before permanent electrical circuits have been energized, test for compliance with requirements.

2. Test completed grounding system at each location where a maximum ground-resistance level is specified, at service disconnect enclosure grounding terminal[, at ground test wells][, and at individual ground rods].  Make tests at ground rods before any conductors are connected.

a. Measure ground resistance not less than two full days after last trace of precipitation and without soil being moistened by any means other than natural drainage or seepage and without chemical treatment or other artificial means of reducing natural ground resistance.

b. Perform tests by fall-of-potential method according to IEEE 81.

Coordinate subparagraph below with "Submittals" Article in Part 1, and edit to suit Project requirements.

3. Prepare dimensioned drawings locating each test well, ground rod and ground rod assembly, and other grounding electrodes.  Identify each by letter in alphabetical order, and key to the record of tests and observations.  Include the number of rods driven and their depth at each location, and include observations of weather and other phenomena that may affect test results.  Describe measures taken to improve test results.

D. Report measured ground resistances that exceed the following values:

See Evaluations for discussion on appropriate ground resistance values.  Listed below are typical maximum permitted values for different grounding applications; retain and edit applicable subparagraphs.  Coordinate with requirements in Sections specifying equipment to be grounded.

1. Power and Lighting Equipment or System with Capacity 500 kVA and Less:  [10] <Insert value> ohms.

2. Power and Lighting Equipment or System with Capacity 500 to 1000 kVA:  [5] <Insert value> ohms.

3. Power and Lighting Equipment or System with Capacity More Than 1000 kVA:  [3] <Insert value> ohms.

4. Power Distribution Units or Panelboards Serving Electronic Equipment:  [1] [3] <Insert value> ohm(s).

5. Substations and Pad-Mounted Equipment:  [5] <Insert value> ohms.

6. Manhole Grounds:  [10] <Insert value> ohms.

7. <Insert application and maximum ground-resistance value> ohms.

E. Excessive Ground Resistance:  If resistance to ground exceeds specified values, notify Architect promptly and include recommendations to reduce ground resistance.

END OF SECTION 260526

	GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
	260526 - 1



