SECTION 16500

INTERIOR LIGHTING
PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

1. Interior lighting fixtures, lamps, and ballasts.

2. Emergency lighting units.

3. Exit signs.

4. Lighting fixture supports.

5. Retrofit kits for fluorescent lighting fixtures.

B. Related Sections include the following:

1. Division 26 Section "Lighting Control Devices" for automatic control of lighting, including time switches, photoelectric relays, occupancy sensors, and multipole lighting relays and contactors.

2. Division 26 Section "[Central Dimming Controls] [Modular Dimming Controls]" for architectural dimming systems.

3. Division 26 Section "Network Lighting Controls" for manual or programmable control systems with low-voltage control wiring or data communication circuits.

4. Division 26 Section "Wiring Devices" for manual wall-box dimmers for incandescent lamps.

5. Division 26 Section "Theatrical Lighting" for theatrical lighting fixtures and their controls.

C. in this Section.

1.3 QUALITY ASSURANCE

Retain one or both of first two paragraphs below to specify qualifications for laboratories providing photometric data to be submitted for lighting fixtures.

A. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by manufacturers' laboratories that are accredited under the National Volunteer Laboratory Accreditation Program for Energy Efficient Lighting Products.

B. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by an independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. Comply with NFPA 70.

Retain paragraph below if FMG compliance is required.  Coordinate with Drawings.

E. FMG Compliance:  Lighting fixtures for hazardous locations shall be listed and labeled for indicated class and division of hazard by FMG.

Mockup lighting fixtures are often part of a typical room or module mockup used to evaluate and demonstrate an overall interior concept, not just lighting.  Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, type, and other details of mockups on Drawings.  Revise wording if only one mockup is required.

F. Mockups:  Provide interior lighting fixtures for room or module mockups, complete with power and control connections.

1. Obtain Architect's approval of fixtures for mockups before starting installations.

2. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

Retain subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 01 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

3. Approved fixtures in mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

1.4 COORDINATION

Retain this Article if Coordination Drawings are required.

A. Coordinate layout and installation of lighting fixtures and suspension system with other construction that penetrates ceilings or is supported by them, including HVAC equipment, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

B. In Interior Lighting Fixture Schedule where titles below are column or row headings that introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

3. Basis-of-Design Product:  The design for each lighting fixture is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by one of the other manufacturers specified.

2.2 LIGHTING FIXTURES AND COMPONENTS, GENERAL REQUIREMENTS

A. Recessed Fixtures:  Comply with NEMA LE 4 for ceiling compatibility for recessed fixtures.

B. Incandescent Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5A.

C. Fluorescent Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5 and NEMA LE 5A as applicable.

D. HID Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5B.

E. Metal Parts:  Free of burrs and sharp corners and edges.

F. Sheet Metal Components:  Steel, unless otherwise indicated.  Form and support to prevent warping and sagging.

G. Doors, Frames, and Other Internal Access:  Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools.  Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position.

H. Reflecting surfaces shall have minimum reflectance as follows, unless otherwise indicated:

1. White Surfaces:  85 percent.

2. Specular Surfaces:  83 percent.

3. Diffusing Specular Surfaces:  75 percent.

4. Laminated Silver Metallized Film:  90 percent.

I. Plastic Diffusers, Covers, and Globes:

1. Acrylic Lighting Diffusers:  100 percent virgin acrylic plastic.  High resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

For K12 pattern acrylic lenses, thickness of 0.125 inch (3.175 mm) is most common for specification grade fixtures.  Thicknesses of 0.100 and 0.125 inch (2.54 and 3.175 mm) are commonly available.

a. Lens Thickness:  At least [0.125 inch (3.175 mm)] <Insert thickness> minimum unless different thickness is indicated.

b. UV stabilized.

2. Glass:  Annealed crystal glass, unless otherwise indicated.

Retain first paragraph below for special applications where freedom from conducted electromagnetic interference is critical.  Coordinate with Interior Lighting Fixture Schedule on Drawings or with "Requirements for Individual Lighting Fixtures" Article.

J. Electromagnetic-Interference Filters:  Factory installed to suppress conducted electromagnetic-interference as required by MIL-STD-461E.  Fabricate lighting fixtures with one filter on each ballast indicated to require a filter.

K. Air-Handling Fluorescent Fixtures:  For use with plenum ceiling for air return and heat extraction and for attaching an air-diffuser-boot assembly specified in Division 23 Section "Diffusers, Registers, and Grilles."

1. Air Supply Units:  Slots in one or both side trims join with air-diffuser-boot assemblies.

2. Heat Removal Units:  Air path leads through lamp cavity.

3. Combination Heat Removal and Air Supply Unit:  Heat is removed through lamp cavity at both ends of the fixture door with air supply same as for air supply units.

4. Dampers:  Operable from outside fixture for control of return-air volume.

5. Static Fixture:  Air supply slots are blanked off, and fixture appearance matches active units.

2.3 BALLASTS FOR LINEAR FLUORESCENT LAMPS

Select ballast type in first paragraph below to specify the default ballast type for linear fluorescent lamps.  Note that most projects will have some applications for linear fixtures requiring ballasts other than the default type selected below.  For such fixtures, indicate the ballast type in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixtures" Article.  See Editing Instruction No. 9 in the Evaluations for discussion of instant-, rapid-, and programmed-start ballasts.

A. Electronic Ballasts:  Comply with ANSI C82.11; [instant] [programmed]-start type, unless otherwise indicated, and designed for type and quantity of lamps served.  Ballasts shall be designed for full light output unless dimmer or bi-level control is indicated.

1. Sound Rating:  [A] [A, except B for T12/HO and T12/Slimline lamp ballasts].

See Evaluations for discussion of harmonic considerations.

2. Total Harmonic Distortion Rating:  Less than [10] [20] percent.

3. Transient Voltage Protection:  IEEE C62.41, Category A or better.

Consider specifying the higher frequency in subparagraph below if fixtures with default ballasts are used in proximity to infrared sensors.

4. Operating Frequency:  [20] [42] <Insert value> kHz or higher.

See Editing Instruction No. 6 in the Evaluations for discussion of lamp current crest factor.

5. Lamp Current Crest Factor:  [1.7] <Insert value> or less.

6. BF:  0.85 or higher.

7. Power Factor:  [0.95] [0.98] or higher.

Delete subparagraph below if instant start is selected as the default ballast type, since parallel lamp operation is standard with that ballast type.  Retain if default ballast is program start and it is important for surviving lamps to operate when one lamp served by a ballast has failed.  There may be a cost premium for this little-used option for program-start ballasts.

8. Parallel Lamp Circuits:  Multiple lamp ballasts shall comply with ANSI C 82.11 and shall be connected to maintain full light output on surviving lamps if one or more lamps fail.

B. Electronic Programmed-Start Ballasts for [T5] [T5HO] [T5 and T5HO] Lamps:  Comply with ANSI C82.11 and the following:

1. Lamp end-of-life detection and shutdown circuit for T5 diameter lamps.

2. Automatic lamp starting after lamp replacement.

3. Sound Rating:  A.

4. Total Harmonic Distortion Rating:  Less than 20 percent.

5. Transient Voltage Protection:  IEEE C62.41, Category A or better.

6. Operating Frequency:  20 kHz or higher.

7. Lamp Current Crest Factor:  1.7 or less.

8. BF:  0.95 or higher, unless otherwise indicated.

9. Power Factor:  [0.95] [0.98] or higher.

C. Electromagnetic Ballasts:  Comply with ANSI C82.1; energy saving, high-power factor, Class P, and having automatic-reset thermal protection.

1. Ballast Manufacturer Certification:  Indicated by label.

D. Single Ballasts for Multiple Lighting Fixtures:  Factory-wired with ballast arrangements and bundled extension wiring to suit final installation conditions without modification or rewiring in the field.

E. Ballasts for Low-Temperature Environments:

1. Temperatures 0 Deg F (Minus 17 Deg C) and Higher:  [Electronic] [Electromagnetic] [Electronic or electromagnetic] type rated for 0 deg F (minus 17 deg C) starting and operating temperature with indicated lamp types.

2. Temperatures Minus 20 Deg F (Minus 29 Deg C) and Higher:  Electromagnetic type designed for use with indicated lamp types.

F. Ballasts for Low Electromagnetic-Interference Environments:  Comply with 47 CFR, Chapter 1, Part 18, Subpart C, for limitations on electromagnetic and radio-frequency interference for consumer equipment.

G. Ballasts for Dimmer-Controlled Lighting Fixtures:  Electronic type.

1. Dimming Range:  100 to [5] <Insert value> percent of rated lamp lumens.

2. Ballast Input Watts:  Can be reduced to [20] <Insert value> percent of normal.

3. Compatibility:  Certified by manufacturer for use with specific dimming control system and lamp type indicated.

H. Ballasts for Bi-Level Controlled Lighting Fixtures:  Electronic type.

1. Operating Modes:  Ballast circuit and leads provide for remote control of the light output of the associated lamp between high- and low-level and off.

a. High-Level Operation:  100 percent of rated lamp lumens.

b. Low-Level Operation:  [30] [50] percent of rated lamp lumens.

2. Ballast shall provide equal current to each lamp in each operating mode.

3. Compatibility:  Certified by manufacturer for use with specific bi-level control system and lamp type indicated.

2.4 FLUORESCENT LAMPS

A. Low-Mercury Lamps:  Comply with EPA's toxicity characteristic leaching procedure test; shall yield less than 0.2 mg of mercury per liter when tested according to NEMA LL 1.

B. T8 rapid-start[ low-mercury] lamps, rated 32 W maximum, nominal length of 48 inches (1220 mm), 2800 initial lumens (minimum), CRI 75 (minimum), color temperature [3500] <Insert value> K, and average rated life 20,000 hours, unless otherwise indicated.

C. T8 rapid-start[ low-mercury] lamps, rated 17 W maximum, nominal length of 24 inches (610 mm), 1300 initial lumens (minimum), CRI 75 (minimum), color temperature [3500] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

D. T5 rapid-start[ low-mercury] lamps, rated 28 W maximum, nominal length of 45.2 inches (1150 mm), 2900 initial lumens (minimum), CRI 85 (minimum), color temperature [3000] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

E. T5HO rapid-start, high-output[ low-mercury] lamps, rated 54 W maximum, nominal length of 45.2 inches (1150 mm), 5000 initial lumens (minimum), CRI 85 (minimum), color temperature [4100] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

F. Compact Fluorescent Lamps:  4-Pin, [low mercury, ]CRI 80 (minimum), color temperature [3500] <Insert value> K, average rated life of 10,000 hours at 3 hours operation per start, [and suitable for use with dimming ballasts, ]unless otherwise indicated.

1. 13 W:  T4, double or triple tube, rated 900 initial lumens (minimum).

2. 18 W:  T4, double or triple tube, rated 1200 initial lumens (minimum).

3. 26 W:  T4, double or triple tube, rated 1800 initial lumens (minimum).

Low-mercury products may not be available in higher-wattage products in three subparagraphs below.  Consult manufacturers.

4. 32 W:  T4, triple tube, rated 2400 initial lumens (minimum).

5. 42 W:  T4, triple tube, rated 3200 initial lumens (minimum).

6. 55 W:  T4, triple tube, rated 4300 initial lumens (minimum).

2.5 HID LAMPS

A. High-Pressure Sodium Lamps:  ANSI C78.42, CRI 21 (minimum), color temperature [1900] <Insert value> K, and average rated life of 24,000 hours, minimum.

1. Dual-Arc Tube Lamps:  Arranged so only one of two arc tubes is lighted at one time and, when power is restored after an outage, the cooler arc tube, with lower internal pressure, lights instantly, providing an immediate 8 to 15 percent of normal light output.

B. Metal-Halide Lamps:  ANSI C78.1372, with a minimum CRI [65] <Insert value>, and color temperature [4000] <Insert value> K.

C. Pulse-Start, Metal-Halide Lamps:  Minimum CRI 65, and color temperature [4000] <Insert value> K.

D. Ceramic, Pulse-Start, Metal-Halide Lamps:  Minimum CRI [80] <Insert value>, and color temperature [4000] <Insert value> K.

2.6 LIGHTING FIXTURE SUPPORT COMPONENTS

Coordinate this Article with Drawings.  See Editing Instruction No. 2 in the Evaluations for discussion of seismic considerations.

A. Comply with Division 26 Section "Hangers and Supports for Electrical Systems" for channel- and angle-iron supports and nonmetallic channel and angle supports.

B. Single-Stem Hangers:  1/2-inch (13-mm) steel tubing with swivel ball fittings and ceiling canopy.  Finish same as fixture.

C. Twin-Stem Hangers:  Two, 1/2-inch (13-mm) steel tubes with single canopy designed to mount a single fixture.  Finish same as fixture.

D. Wires:  ASTM A 641/A 641M, Class 3, soft temper, zinc-coated steel, [12 gage (2.68 mm)] <Insert wire size>.

Coordinate first paragraph below with Drawings to identify humid spaces.

E. Wires for Humid Spaces:  ASTM A 580/A 580M, Composition 302 or 304, annealed stainless steel, [12 gage (2.68 mm)] <Insert wire size>.

F. Rod Hangers:  3/16-inch (5-mm) minimum diameter, cadmium-plated, threaded steel rod.

G. Hook Hangers:  Integrated assembly matched to fixture and line voltage and equipped with threaded attachment, cord, and locking-type plug.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Lighting fixtures:  Set level, plumb, and square with ceilings and walls.  Install lamps in each fixture.

B. Support for Lighting Fixtures in or on Grid-Type Suspended Ceilings:  Use grid as a support element.

1. Install a minimum of four ceiling support system rods or wires for each fixture.  Locate not more than 6 inches (150 mm) from lighting fixture corners.

2. Support Clips:  Fasten to lighting fixtures and to ceiling grid members at or near each fixture corner with clips that are UL listed for the application.

3. Fixtures of Sizes Less Than Ceiling Grid:  Install as indicated on reflected ceiling plans or center in acoustical panel, and support fixtures independently with at least two 3/4-inch (20-mm) metal channels spanning and secured to ceiling tees.

4. Install at least one independent support rod or wire from structure to a tab on lighting fixture.  Wire or rod shall have breaking strength of the weight of fixture at a safety factor of 3.

C. Suspended Lighting Fixture Support:

1. Pendants and Rods:  Where longer than 48 inches (1200 mm), brace to limit swinging.

2. Stem-Mounted, Single-Unit Fixtures:  Suspend with twin-stem hangers.

3. Continuous Rows:  Use tubing or stem for wiring at one point and tubing or rod for suspension for each unit length of fixture chassis, including one at each end.

D. Air-Handling Lighting Fixtures:  Install with dampers closed and ready for adjustment.

E. Adjust aimable lighting fixtures to provide required light intensities.

F. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Test for Emergency Lighting:  Interrupt power supply to demonstrate proper operation.  Verify transfer from normal power to battery and retransfer to normal.

B. Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results.  If adjustments are made to lighting system, retest to demonstrate compliance with standards.

END OF SECTION 265100

INTERIOR LIGHTING
265100 - 1

