SECTION 16425
SWITCHBOARDS
PART 1 -  GENERAL

1.01 RELATED DOCUMENTS

A. Drawings
B. General provisions of the Contract, including General and Supplementary Conditions
C. Refer to Division 16 Sections for the following:
1. Electrical Basic Requirements

2. Overcurrent Protective Devices

3. Low Voltage Power Circuit Breakers

4. Service Equipment

1.02 SUMMARY

D. Scope:

Extent of switchboard work required by this Section is indicate don drawings and schedules and by requirements of this Section and Section 16010, “Basic Electrical Requirements.”
E. Types:

Switchboards specified in this Section are of the metal enclosed deadfront distribution type.

1.03
SUBMITTALS

A.
Division 1:  Conform to the requirements of Division 1, Section 01300, ‘Submittals.”

B.
Product Data:  Submit manufacturer’s data on switchboards including, but not limited to the following:
1.
Indicate service voltage, number of phases, and frequency.

2.
Show main bus ampacity rating and short circuit current rating.

3.
Indicate overcurrent protective device types and ratings.

4.
Indicate metering equipment types and functions.

F. Shop Drawings:  Submit shop drawings, sufficient in detail to verify that the equipment meets all specified requirements.  Include the following on shop drawings:
1. Show overall dimensions of enclosures.
2. Show front and side views of enclosures.

3. Provide nameplate legends.

4. Show single line diagram.

5. Indicate size and number of bars per phase and neutral in each bus run including through, section and branch buses plus the equipment ground buses.

6. Show electrical characteristics of the equipment, including ampere ratings of buses, maximum short circuit withstand ratins and control voltages.

7. Show features, characteristics and ratings of individual overcurrent protective devices.

8. Provide internal wiring diagrams.

G. Maintenance Manuals:
 Provide operation and maintenance manuals for all switchboards furnished under this Section.  Include instructions for operation and maintenance and spare parts data.
1.04
QUALITY ASSURANCE

A.
Codes and Standards

Conform to the following:

1. National Electrical Manufacturers Association (NEMA):
a. PB 2 Deadfront Distribution Switchboards

b. PB 2.1 General Instructions for Proper Handling, Installation, Operation and Maintenance of Deadfront Distribution Switchboards Rated 600 Volts or Less.

2. Comply with national Fire Protection Associations (NFPA) 70, “National Electrical Code.”

3. Underwriters Laboratories, Inc. (UL)

a. 486A Wire Connectors and Soldering Lugs for Use with Copper Conductors

b. 891 Dead-Front Switchboards

c. 977 Fused Power-Circuit Devices.

4. Provide all devices UL listed and labeled.

H. Certification:  Provide certificate of compliance with the referenced standards from the manufacturer of the switchboard.
1.05 DELIVERY, STORAGE, AND HANDLING

I. Delivery: Handle equipment carefully to prevent damage.  Do not install damaged switchboards.  Replace with new.
J. Storage:
Store equipment in a clean, dry place.  Protect from weather, dirt, water, construction debris, and physical damage.
PART 2 -  PRODUCTS

2.01 MANUFACTURERS

2.02
SWITCHBOARDS
A. Provide self-supporting, freestanding switchboards consisting of stationary structures on and within which are mounted overcurrent protective devices, buses, barriers and other components.
B. Basic arrangement:

1. Provide basic arrangement and type of mounting for overcurrent protective devices as indicated on the drawings:

a. 400, 600, 800 amp fused switches as scheduled on the drawings.

b. Provide panel mounted feeder protective devices as scheduled for MDP.

C. Structure:

Construct the switchboard of a structural or formed steel frame, braced and bolted or welded into a rigid structure.  Provide structural strength to maintain alignment and prevent damage in shipment and erections, or from stresses resulting from short circuits.  Bolted construction with tack welded joints is acceptable.  Provide additional construction features as follows:
1. Completely enclose the frame on the front, rear, top and sides with sheet steel covered, doors and panels.  Provide accessibility from both front and rear, except as otherwise specified.
2. Provide hinged steel rear access doors, No. 12 MSS gauge minimum, with captive thumb nuts or quarter turn screws.

3. Provide hinged panels on the front covering each individually mounted breaker and each instrument, metering or blank compartment.

4. Provide the hinged covers with latches, and with cutouts where necessary for ventilation, operating mechanisms, mechanical trips, and positions indicators.

5. Provide adequate ventilating louvers in the hinged panels as required to limit the temperature rise of current-carrying parts, including contacts, to acceptable values.

D. Pull Boxes:
Where indicated on project drawings or required by installation conditions, provide a pull box of the same type of construction as the switchboard.  Mount pull box on the top of the switchboard and provide ventilation to maintain temperature within same limits as required for the switchboard.
1. Adequate ventilation to maintain temperature in pull box within same limits as switchboard.

2. Set back from front to clear circuit-breaker removal mechanism.

3. Removable covers shall form top, front, and sides.  Top covers at rear shall be easily removable for drilling and cutting.

4. Bottom shall be insulating, fire-resistive material with separate holes for cable drops into switchboard.

5. Cable supports shall be arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

E. Buses and Connections:  Three phase, four wire unless otherwise indicated.

1. Provide buses and connections of hard-drawn copper of 98 percent conductivity or high strength electrical grade aluminum alloy.

2. If aluminum bus is used, provide feeder and circuit breaker connections of copper or tin-plated aluminum.

3. Size, configure and brace the bus bars, the insulated bus mounting supports, the insulated spacer supports and the structure housing to safely withstand the short circuit currents which may be imposed.  Provide the integrated shor circuit rating for each switchboard as indicated on the drawings.

4. Bolt or weld bus connections and provide laminations arranged to secure amply contact area.

5. Plate all contract surfaces of bus bars.  A ring silver plating method using ½ mil of silver under bolt heads accurately aligned will be acceptable.

6. Space bus laminations a minimum of ¼ inch apart.

7. Where aluminum bus is used. Make the connections between sections with plated nuts and bolts or aluminum nuts and bolts with a flat plated steel washer against the aluminum and a plated spring type conical steel washer under the nut.

8. Provide adequate pressure at bus joints using precision torque wrenches calibrated to the specific foot-pound requirements recommended by the manufacturer.

9. Provide access to permit checking of bolt tightness.

10. Do not use calbe for power interconnectiosn between circuit breaker compartments.  Provide copper or aluminum bus bar.

11. For short circuit duty 100,000 amperes asymmetrical and below, use solderless clamp type lugs at circuit breaker bus extensions to accommodate cable attached thereto.  For highs short circuit duty use compression lugs.

12. Provide main phase buses, neutral bus and equipment ground bus the entire length of the assembly without reducing bus capacity.  Make provision for future extensions from either end by means of bolt holes or other approved method except as otherwise indicated on drawings.

F. Ground and Neutral Buses:

Provide each switchboard section with a bare neutral bus on insulated bus supports except as herein noted and an uninsulated 1/4 ” x 2” copper equipment ground bus bar secured to each unit frame and suitably bolted ot the related bus bars in the adjacent sections to provide separate, integrated continuous, neutral and equipment ground buses.
1. Provide the neutral bus for the 3-phase, 4-wire system with the same ampacity as the associated phase buses unless otherwise indicated on drawings.
2. Provide the switchboard ground bus with minimum ampacity to meet NFPA 70 requirements for a system ground conductor and arrange it to ground the switchboard noncurrent-carrying parts.  Provide brazed or approved pressure connector terminations for the feeder and branch circuit ground conductors.

PART 3 -  EXECUTION

3.01 INSTALLATION

A. Install switchboards and accessories according to NEMA PB 2.1, NFPA 70, and the manufacturer’s instructions.
B. Locations and Layout:

The exact relative locations (and physical layout) of equipment in the switchboard may be varied as required to suit manufacturer’s design, provided the required functions and operations are accomplished; however, the identification of the units as indicated on drawings shall be followed exactly to facilitate checking and building maintenance procedures.

C. Anchoring:
Anchor each switchboard assembly to two 4-inch minimum channel iron sills, by tack welding or bolting.
1. Provide sills that suit the switchboard, and level and ground them flush into the floor.
2. Where a membrane waterproofed floor or pressure slab is indicated under a switchboard locations, provide a 4-inch high reinforced concrete pad.  Pour the pad separately on top of the finished floor slab and arrange it to extend two inches beyond the base of the switchboard all around.

3. Embed the 4-inch channel sills specified above in the concrete pad.

D. Cleaning and Touchup:
Clean all dirt and debris from the inside and outside of the switchboard before placing in operation.  Touchup scratched or marred surfaces to match original finish.
E. Connections:

Tighten field connected connectors and terminals, including screws and bolts, in accordance with equipment manufacturer’s published torque tightening values.  Where manufacturer’s torquing requirements are not indicated, tighten connectors and terminals to comply with tightening torques specified in UL 486A.
F. Adjustment:
Adjust all operating mechanisms and moving parts for free mechanical movement.

G. Tests prior to energizing:  Perform the following electrical tests:
1. Check with ground resistance tester phase-to-phase and phase-to-ground insulation resistance levels to ensure requirements are fulfilled.

2. Check for electrical continuity of circuit, and for short-circuits.

H. Demonstration:
Subsequent to wire and cable hook-ups, energize switchboards and demonstrate functioning of all devises and components.

I. Instructions:
Furnish the services of a competent instructor for one 3-hour period for instructing personnel in the operation and maintenance of the switchboard.

END OF SECTION
08112.13 / Crosswinds Apartments
16425 - 1
SWITCHBOARDS

