SECTION 16470

PANELBOARDS
PART 1 -  GENERAL

1.01 RELATED DOCUMENTS

A. Drawings
B. General provisions of the Contract, including General and Supplementary Conditions
C. Division 01 Specification Sections
D. Section 16010 – Basic Electrical Requirements.  Extent of panelboard work is indicated by Drawings and Schedules.

1.02 SUMMARY

A. The work of the section consists of providing labor, materials, tools, appliances and miscellaneous accessories associated with panelboard work indicated herein and on the drawings and schedules.

B. Types of panelboards and enclosure required for this project include the following:

1. Power- Distribution panelboards.

2. Lighting and appliance panelboards.

PART 2 -  PRODUCTS

2.01
MANUFACTURERS
A. Manufacturers:  Subject to compliance with requirements, provide products by one of the following (for each type of panelboard and enclosure::

1. General Electric Company; GE Consumer & Industrial.

2. ITE.
3. Square D.

2.02
Panelboards:
Except as otherwise indicated, provide panelboards enclosure and ancillary components, of types, sizes, and ratings indicated, which comply with manufacturer’s standard materials, design and construction in accordance with published products information; equip with number of unit panelboard devices as required for complete installation.

B. Where types, sizes, or ratings are not indicated, comply with NEC, UL and established industry standards for applications indicated.
C. Lighting and appliance panelboards shall be dead front safety-type equipped with molded case circuit breakers as shown and scheduled.

D. Main lugs or main overcurrent units shall be furnished for panelboards as indicated on the drawings.

E. The number of branches in each panel shall be as indicated on the drawings.

F. Panelboards shall be mounted in code gauge galvanized sheet steel cabinets with corners lapped and riveted or fastened by other approved methods.  Cabinets shall be of such size as to allow a wiring gutter space of at least 6” all around for power panels, and 4” all around for lighting panels.  Extra large gutter spaces shall be provided is specifically called for.

G. Panelboards shall be flush or surface mounted as indicated on the Drawings.  Trim for each panel shall be suitable for the type of mounting.  Each trim shall be complete with suitable hinged door having chrome plated flush type combination lock and catch, except that for doors over 48” in height a chrome plated vault handle and 3 point catch shall be provided with built-in lock arranged to fasten door at top, bottom and center.  Two keys shall be provided for each lock and each key shall open all panelboards furnished.  All trims shall be of a type that is self-supporting on the box after the trim holding screws have been removed.  All free-standing cabinets shall be secured to floors, walls, and columns with approved angle iron or unistrut framework.  Framework shall be painted as cabinets.
H. Each panelboard shall be complete with main copper or aluminum bus run up the center and neutral bars where required and all proper sequence phase connections.  Polarized panelboards will not be accepted.  Capacities of copper busses and connections shall be based on a maximum density of 1000 amps per sq. in.  Spacing of busses shall not be less than code requirements.  Busses shall be arranged for single or 3-phase, 3- or 4- wire supply as indicated on the Drawings.  Busses shall be provided with suitable phase identification.

I. Directory holder with metal frame shall be furnished and installed upon door of each cabinet, with complete typewritten circuit schedule inserted.

J. The inside and outside of panelboard boxes, doors and trims shall be furnished with at least two coats of manufacturer’s standard finish paint over a baked-on prime coat.

K. Provide ground bus.  Provide additional isolated ground bus where specified.

L. Lighting and Appliance Panels:  Panels shall be for use on 208/120 volt, 3 phase, 4-wire, 60 cycle, solid neutral service, with number and size of bolt-on type circuit breaker branches as shown on the Drawings.  Circuit breaker’s interrupting capacity shall be 10,000 RMS symmetrical amperes unless otherwise noted.

M. Power and Distribution Panels:
1. Power and distribution panels shall be the dead-front type, without hinged doors, with fusible switches or circuit breakers in the branches as indicated on the Drawings.  The panels shall be suitable for 208Y/120 volt, 3-phase, 4-wire supply as shown.  Fused switches or circuit breakers shall be quick-make, quick-break with provision for “lock-out” in the open position and provided with circuit designation.

2. Provide distribution panel circuit breakers with conventional interrupting capacity, high interrupting capacity, or integral current limiters as shown.  Circuit breakers shall be conventional interrupting capacity unless otherwise shown, but in no case less than the following symmetrical amperes RMS:

FRAME SIZE/


CONVENTIONAL

HIGH



INTEGRAL

VOLTAGE


INTERRUPTING

INTERRUPTING
CURRENT







CAPACITY



CAPACITY


LIMITERS

100A/240V


10,000 AIC



22,000 AIC


200,000 AIC

225A/240V


10,000 AIC



22,000 AIC


200,000 AIC

400A/240V


22,000 AIC



25,000 AIC


200,000 AIC

600A/240V


42,000 AIC



65,000 AIC


200,000 AIC

800A/240V


42,000 AIC



65,000 AIC


200,000 AIC

1000A/240V


42,000 AIC



65,000 AIC


200,000 AIC

1200A/240V


42,000 AIC



65,000 AIC


200,000 AIC

N. Series rated circuit breaker panels shall not be accepted.
PART 3 -  EXECUTION

3.01
INSTALLATION
A. Install panelboards and enclosures where indicated, in accordance with manufacturer’s written instructions, applicable requirements of NEC and NECA’s “Standard of Installation,” and in compliance with recognized industry practices to ensure that products fulfill requirements.
B. Coordinate installation of panelboards and enclosures with cable and raceway installation work.

C. Anchor panelboard assemblies firmly to walls and structural surfaces, ensuring that they are permanently and mechanically secure.

D. Provide properly wired electrical connections for panelboards within enclosures.

E. Fill out (typewritten) panelboard’s circuit directory card upon completion of installation work.

F. Tighten connectors and terminals, including screws and bolts, in accordance with equipment manufacturer’s published torque tightening values for equipment connectors.  Where manufacturer’s torquing requirements are not indicated, tighten connectors and terminals to comply with tightening torques specified in UL Stds 486A and B.

3.02 GROUNDING
A. Provide equipment grounding connections for panelboard enclosures as indicated.  Tighten connections to comply with UL tightening torques to assure permanent and effective grounds.
3.03
FIELD QUALITY CONTROL

A.
Prior to energization of panelboards, check with ground resistance tester phase-to-phase and phase-to-ground insulation resistance levels to ensure requirements are fulfilled.
B.
Prior to energization, check panelboards for electrical continuity of circuits, and for short-circuits.

3.04
ADJUSTING AND CLEANING
A.
Adjust operating mechanisms for free mechanical movement.

B.
Touch-up scratched or marred surfaces to match original finishes.

3.05 DEMONSTRATION
A. Subsequent to wire and cable hook-ups, energize panelboards and demonstrate functioning in accordance with requirements.  Where necessary, correct malfunctioning units, and then retest to demonstrate compliance.
B. Label panelboards in accordance with SECTION 16195.

END OF SECTION
08112.13 / Crosswinds Apartments
16470 - 1
PANELBOARDS

