SECTION 16123PRIVATE 

BUILDING WIRE AND CABLE

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.

seq level0 \h \r0 

seq level1 \h \r0 

seq level2 \h \r0 

seq level3 \h \r0 

seq level4 \h \r0 

seq level5 \h \r0 

seq level6 \h \r0 

seq level7 \h \r0 PART 1 – GENERAL


1.01

SECTION INCLUDES



A.
Building wire and cable.



B.
Underground feeder and branch circuit cable.



C.
Service entrance cable.



D.
Wiring connectors and connections.


1.02
seq level2 \h \r0 
RELATED SECTIONS



A.
Section 16111 ‑ Conduit.



B.
Section 16195 ‑ Identification.


1.03

seq level2 \h \r0 

REFERENCES



A.
ANSI/NFPA 70 ‑ National Electrical Code.



B.
Reference to General Conditions.


1.04

seq level2 \h \r0 

SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Manufacturer's Installation Instructions: Indicate application conditions and limitations of use stipulated by product testing agency specified under Regulatory Requirements.


1.05
seq level2 \h \r0 
QUALIFICATIONS



A.
Manufacturer:  Company specializing in manufacturing products specified in this Section with minimum three  years experience.


1.06
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Furnish products listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and shown.


1.07
seq level2 \h \r0 
FIELD SAMPLES




Not Used


1.08

seq level2 \h \r0 

PROJECT CONDITIONS



A.
Verify that field measurements are as shown on Drawings.



B.
Conductor sizes are based on copper.



C.
Wire and cable routing shown on Drawings is approximate unless dimensioned.  Route wire and cable as required to meet Project Conditions.



D.
Where wire and cable routing is not shown, and destination only is indicated, determine exact routing and lengths required.


1.09
seq level2 \h \r0 
COORDINATION



A.
Coordinate Work under provisions of Section 01039.

PART 2 – PRODUCTS


2.01

MANUFACTURES – BUILDING WIRE AND CABLE




Not Used


2.02
seq level2 \h \r0 
BUILDING WIRE AND CABLE



A.
Description:  Single conductor insulated wire.



B.
Conductor:
Copper.



C.
Insulation ANSI/NFPA 70, Type THHN/THWN.

seq level1 \h \r0 

seq level2 \h \r0 

seq level3 \h \r0 PART 3 – EXECUTION


3.01

EXAMINATION



A.
Verify that interior of building has been protected from 




weather.



B.
Verify that mechanical work likely to damage wire [and cable] has been completed.


3.02

seq level2 \h \r0 

PREPARATION



A.
Completely and thoroughly swab raceway before installing wire.


3.03

seq level2 \h \r0 

WIRING METHODS



A.
Concealed Dry Interior Locations:  Use only building wire, Type THHN/THWN insulation, in raceway.



B.
Exposed Dry Interior Locations:  Use only building wire, Type THHN/THWN insulation, in raceway.



C.
Above Accessible Ceilings:  Use only building wire, Type THHN/THWN insulation, in raceway.



D.
Wet or Damp Interior Locations:  Use only building wire, Type THHN/THWN insulation, in raceway.



E.
Exterior Locations:  Use only building wire, Type THHN/THWN insulation, in raceway.



F.
Use wiring methods indicated on Drawings.


3.04

seq level2 \h \r0 

INSTALLATION



A.
Install products in accordance with manufacturers instructions.



B.
Use solid conductor for feeders and branch circuits 10 AWG and smaller.



C.
Use stranded conductors for control circuits.



D.
Use conductor not smaller than 12 AWG for power and lighting circuits.



E.
Use conductor not smaller than 16 AWG for control circuits.



F.
Use 10 AWG conductors for 20 ampere, 120 volt branch circuits longer than 75  feet.



G.
Use 10 AWG conductors for 20 ampere, 277 volt branch circuits longer than 200 feet.



H.
Pull all conductors into raceway at same time.



I.
Use suitable wire pulling lubricant for building wire 4 AWG and larger.



J.
Protect exposed cable from damage.



K.
Use split bolt connectors for copper conductor splices and taps, 6 AWG and larger.  Tape uninsulated conductors and connector with electrical tape to 150 percent of insulation rating of conductor.



L.
Use solderless pressure connectors with insulating covers for copper conductor splices and taps, 8 AWG and smaller.



M.
Use insulated spring wire connectors with plastic caps for copper conductor splices and taps, 10 AWG and smaller.


3.05

seq level2 \h \r0 

INTERFACE WITH OTHER PRODUCTS



A.
Identify wire and cable under provisions of Section 16195.



B.
Identify each conductor with its circuit number or other designation indicated on Drawings.


3.06

seq level2 \h \r0 

FIELD QUALITY CONTROL



A.
Perform field inspection and testing under provisions of Section 01400.



B.
Inspect wire for physical damage and proper connection.



C.
Measure tightness of bolted connections and compare torque measurements with manufacturer's recommended values.



D.
Verify continuity of each branch circuit conductor.

END OF SECTION

PAGE  
08112.13 / Crosswinds Apartments 
16123 - 1 
BUILDING WIRE AND CABLE

