SECTION 16450

GROUNDING
PART 1 -  GENERAL

1.1 DESCRIPTION
A. System Grounding
1. Secondary service neutrals shall be grounded at the supply side of the switchboard.
2. Separately derived systems (transformers downstream from the service entrance) shall have the secondary neutral grounded.

3. Isolation transformers and isolated power systems shall not be system grounded.

B. Equipment Grounding

1. Metallic structures, enclosures, raceways, outlet boxes, junction boxes, cabinets, machine frames and other conductive items in close proximity with electrical circuits shall be grounded for personal safety and to provide a low impedance path for possible ground fault currents.

PART 2 -  PRODUCTS

2.1 Materials
A. Grounding Wires
1. Shall be NEC-approved and UL-labeled types, copper with TW or better insulations, color-identified green except where otherwise shown on drawings or specified.

2. Wire size shall not be less than shown on drawings and not less than required by NEC.

B. Ground Rods:

1. Were required, ground rods shall be copper clad steel, 5/8” diameter by 10’ long.
C. Accessories:

1. Provide all necessary clamps and connectors sized for the ground rods and wires being used.
PART 3 -  EXECUTION

3.1 INSTALLATION
A. Grounding shall be in accordance with NEC, as shown on drawings and as hereinafter specified for the respective equipment.
B. Outdoor Fences:  Connect outdoor fences around electrical equipment to grounding electrode system.

C. Metallic Conduit:  Metallic conduits, which terminate without mechanical connection to a housing of electrical equipment by means of locknut and bushings or adaptors, shall be provided with grounding bushings.  Bushings shall be connected with a bare grounding conductor to equipment ground bus.

3.2 SECONDARY EQUIPMENT & CIRCUITS
A. Main Bonding Jumper:  Connect the secondary service neutral to ground bus in service equipment.
B. Water Pipe and Supplemental Electrode:
1. Grounding electrode conductor – provide a connections between the main service equipment ground bus and the metallic water pipe system only on the supply side of the water meter.

2. Connect the ground from the main service equipment to the ground system between the water pipe on the supply side of water meter, to the pad-mounted transformer ground system and to the rebar ground system mentioned in the next paragraph.

3. When possible, rebars in footings at least 3’ deep and at least 20’ long shall be used in the ground system by bonding with exothermic welds or approved bronze ground clamps holding at least 2/0 copper wire to the bonding point, and extending the conductor out of the concrete through a raceway to service entrance equipment ground.

C. Main Service Equipment (Separate Individual Enclosure):  Provide a ground bar bolted ot the enclosure with lugs for connecting the various grounding conductors.
1. Connect the various feeder green grounding conductors to the ground bus in the enclosure with suitable pressure connectors.

2. Connect grounding electrode conductor the ground bus.

3. Connect the neutral to the ground bus (main bonding jumper)

4. Connect metallic conduits, which terminate without mechanical connection to the housing, by grounding bushings and ground wire to the ground bus.

D. Conduit Systems:
1. Ground all metallic conduit systems.

2. Nonmetallic conduit systems shall contain a grounding conductor.

3. Conduit provided for mechanical protection and containing only a grounding conductor shall be bonded to that conductor at the entrance and exit from the conduit.

E. Feeders and branch Circuits:  Install green grounding conductors with feeders and branch circuits as follows:
1. All feeders

2. All receptacle and lighting branch circuits

3. Motors and motor controllers for 3 phase motors only.

4. Fixed equipment and appliances
5. Items of equipment where the final connections is made with flexible metal conduit shall have a grounding wire

6. Additional locations and systems as shown on drawings.

F. Boxes, Cabinets, Enclosures and Panelboards:
1. Bond grounding wires to each appropriate pullbox, junction box, outlet box, cabinets and other enclosures through which ground wires pass.

2. Provide lugs in each box and enclosure for ground wire termination.

3. Provide ground bars in panelboards bolted to the housing with sufficient lugs for terminating the ground wires.

G. Motors and Starters:
1. Provide lugs in motor terminal box and starter housing for ground wire termination.

2. Make ground wire connections to ground bus in motor control centers.

H. Receptacles not approved for grounding through their mounting screws shall have a ground wire from green ground terminal to the outlet box ground screw.

I. Lighting Fixtures:  Shall be grounded through the conduit systems.  Fixtures connected with flexible conduit shall have a green ground wire included with the power wires from the fixture through the flexible conduit to the first outlet box.

J. Lighting Fixtures:  Shall be grounded with the branch circuit grounding conductor.

K. Electrical Appliances and Equipment:  Fixed electrical appliances and equipment shall have a ground lug installed for termination of green ground conductor.

L. Light fixture switches:  Shall be grounded type.

3.3 CONDUCTIVE PIPING, DUCTS
A. Bond conductive piping systems and ducts in the building to the electrical system ground.  Bonding connections shall be made as close as practicable to the building ground system.
3.4 GROUND RESISTANCE
A. Grounding system shall be tested to insure that ground resistance does not exceed 5 ohms.
B. Services at power company interface points shall comply with the power company ground resistance requirements.

3.5 GROUND ROD INSTALLATION
A. Distance:  Drive each rod vertically for not less than 10’.
B. Multiple Rods:  Where required to obtain specified ground resistance, install multiple rods not closer than 6’ between each rod.

C. Where ground connections will be permanently concealed, make connections by the exothermic process to form solid metal joints or approved bronze connectors.  Make accessible ground connections with mechanical pressure type ground connectors.
D. Where rock prevents the driving of vertical ground rods, install grounding electrodes in horizontal trenches to achieve the specified resistance.

END OF SECTION

08112.13 / Crosswinds Apartments
16450 - 2
GROUNDING

