

SECTION 15623PRIVATE 


FORCED AIR COOLING AND HEATING

PART 1   GENERAL


1.01
SECTION INCLUDES



A.
Forced air furnaces.



B.
Refrigerant cooling coil and condenser.



C.
Controls.


1.02
RELATED SECTIONS



A.
NOT USED

1.03
REFERENCES



A.
ANSI/ASHRAE 15 ‑ Safety Code for Mechanical Refrigeration.



B.
ANSI/ASHRAE ‑ 90A ‑ Energy Conservation in New Building Design.



C.
ANSI/ASHRAE ‑ 103 ‑ Heating Seasonal Efficiency of Central Furnaces and Boilers, Methods of Testing.



D.
ANSI/NEMA MG 1 ‑ Motors and Generators.



E.
ANSI/NFPA 90B ‑ Installation of Warm Air Heating and Air Conditioning Systems.

F. ANSI/UL 207 ‑ Refrigerant ‑ Containing Components and Accessories, Non‑Electrical.

G. ARI 270 – Sound Rating of Outdoor Unitary Equipment.

H. ARI 520 – Positive Displacement Refrigerant Compressors, Compressor Units and Condensing Units.

I. ASHRAE 14 – Methods of Testing for Rating Positive Displacement Condensing Units.

J. ASHRAE 52 – Method of Testing Air Cleaning Devices Used in General Ventilation for Removing Particulate Matter.



K.
FS F‑F 310A ‑ Filter, Air Conditioning: Viscous Impingement and Dry Types, Replaceable.



L.
MIL‑F‑17104E ‑ Furnaces, Warm Air and Heaters, Unit, Forced Air Circulation, Oil‑ and Gas‑Fired.



M.
NFPA 90A ‑ Installation of Air Conditioning and Ventilating Systems.


1.04
SUBMITTALS



A.
Submit shop drawings under provisions of Section 01300.



B.
Submit shop drawings indicating assembly, required clearances, and location and size of field connections.



C.
Product Data: Provide rated capacities, weights, accessories, electrical nameplate data, and wiring diagrams.



D.
Design data: Indicate refrigerant pipe sizing.



E.
Manufacturer's Installation Instructions: Indicate rigging, assembly, and installation instructions.


1.05
OPERATION AND MAINTENANCE DATA



A.
Submit operation data under provisions of Section 01700.



B.
Include manufacturer's descriptive literature, operating instructions, installation instructions, maintenance and repair data, and parts listing.


1.06
QUALITY ASSURANCE



A.
Perform Work in accordance with ANSI/ASHRAE 15.



B.
Maintain one copy of each document on site.


1.07
WARRANTY



A.
Provide ten year warranty under provisions of Section 01700.



B.
Warranty: Include coverage for heat exchangers and compressors.


1.08
EXTRA MATERIALS



A.
Submit maintenance materials under provisions of Section 01700.



B.
Provide two of each filter under provisions of Section 01700.

PART 2   PRODUCTS


2.01
MANUFACTURED :UNITS



A.
Configuration: Upflow type with electric heat and electric refrigeration.



B.
Units: MIL‑F‑17104E; Self‑contained, packaged, factory assembled, pre‑wired unit consisting of cabinet, supply fan, electric heat unit, controls, air filter, refrigerant cooling coil and outdoor package containing compressor, condenser coil and condenser fan.



C.
Construction and Ratings: In accordance with ARI 210/240 and ANSI/UL 207 and ANSI/UL 303.  Testing: ASHRAE 14.



D.
Performance Ratings: Energy Efficiency Rating (EER) not less than (13).



E.
Heating Capacity: See schedule on drawings.



F.
Air Handling: See schedule on drawings.



G.
Cooling Capacity: See schedule on drawings.


2.02
FABRICATION



A.
Cabinet: Galvanized steel with baked enamel finish, easily removed and secured access doors, glass fiber or asbestos insulation and reflective liner and welded steel base.



B.
Supply Fan: Centrifugal type rubber mounted with direct or belt drive, adjustable variable pitch motor pulley.



C.
Air Filters: FS F‑F‑300A; 1 inch (25 mm) thick glass fiber, disposable type arranged for easy replacement.


2.03
HEATER



A.
Provide and install 3 KW electric heat package.


2.04
EVAPORATOR COIL



A.
Coil: Copper tube aluminum fin assembly, galvanized drain pan, drain connection, refrigerant piping connections and factory installed thermostatic expansion valve.


2.05
REFRIGERATION PACKAGE



A.
Compressor: ARI 520; hermetic, 3600 rpm maximum, resiliently mounted integral with condenser, with positive lubrication, crankcase heater, high pressure control, motor overload protection, service valves and drier.



B.
Air Cooled Condenser: ARI 520; aluminum fin and copper tube coil, with direct drive axial propeller fan resiliently mounted, galvanized fan guard.


2.06
REFRIGERATION OPERATING CONTROLS



A.
Room Thermostat: Cycles compressor, condenser fan and supply fan to maintain room temperature setting for heat and cool.

2.07
OPERATING CONTROLS



A.
Adjustable Room Thermostat: Low voltage, to heater operation, compressor and condenser fan and supply fan to maintain temperature setting.  Include systems selector switch (heat‑off‑cool) and fan control switch (auto‑on).



B.
Clubhouse System shall have Electric solid state microcomputer based room thermostat with remote sensor.



C.
Room thermostat to incorporate:




1.
Automatic switching from heating to cooling.




2.
Preferential rate control to minimize overshoot and deviation from set point.




3.
Set‑up for four separate temperatures per day.




4.
Instant override of setpoint for continuous or timed period from one hour to 31 days.




5.
Short cycle protection.




6.
Programming based on weekdays, Saturday and Sunday.




7.
Switch selection features including imperial or metric display, 12 or 24 hour clock, keyboard disable, remote sensor, fan on‑auto.



D.
Room thermostat display to include:




1.
Time of day.




2.
Actual room Temperature.




3.
Programmed temperature.




4.
Programmed time.




5.
Duration of timed override.




6.
Day of week.




7.
System model indication: heating, cooling, auto, off, fan auto, fan on.




8.
State (heating or cooling) operation.

PART 3   EXECUTION


3.01
EXAMINATION



A.
Verify that floors are ready for installation of units and openings are as indicated on shop drawings.  Verify that supports for air cooled condensers are completed.



B.
Verify that proper power supply is available for furnace and condenser package.



C.
Verify that proper fuel supply is available for connection.


3.02
INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Install to NFPA 90A and ANSI/NFPA 90B.



C.
Mount air cooled condenser‑compressor package on vibration isolators.


END OF SECTION

Crosswinds Apartments
15623 - 4
FORCED AIR COOLING & HEATING

