SECTION 16111PRIVATE 

CONDUIT

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.

PART 1 – GENERAL


1.01

SECTION INCLUDES



A.
Metal conduit.



B.
Flexible metal conduit.



C.
Liquid tight flexible metal conduit.



D.
Electrical metallic tubing.



E.
Nonmetal conduit.



F.
Electrical nonmetallic tubing.



G.
Flexible nonmetallic conduit.



H.
Fittings and conduit bodies.


1.02

RELATED SECTIONS



A.
NOT USED.


1.03

REFERENCES



A.
ANSI C80.1 ‑ Rigid Steel Conduit, Zinc Coated.



B.
ANSI C80.3 ‑ Electrical Metallic Tubing, Zinc Coated.



C.
ANSI C80.5 ‑ Rigid Aluminum Conduit.



D.
ANSI/NEMA FB 1 ‑ Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit and Cable Assemblies.



E.
ANSI/NFPA 70 ‑ National Electrical Code.



F.
NECA "Standard of Installation."



G.
NEMA RN 1 ‑ Polyvinyl Chloride (PVC) Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit.



H.
NEMA TC 2 ‑ Electrical Plastic Tubing (EPT) and Conduit (EPC‑40 and EPC‑80).

I. NEMA TC 3 ‑ PVC Fittings for Use with Rigid PVC Conduit and Tubing.



J.
Reference to General Conditions.


1.04

DESIGN REQUIREMENTS



A.
Conduit Size:  ANSI/NFPA 70.


1.05

SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data:  Provide for metallic conduit, flexible metal conduit, liquidtight flexible metal conduit, metallic tubing, nonmetallic conduit, flexible nonmetallic conduit, nonmetallic tubing, fittings, conduit bodies.


1.06

PROJECT RECORD DOCUMENTS



A.
Submit under provisions of Section 01700.



B.
Accurately record actual routing of conduits larger than 2 inches.


1.07

DELIVERY, STORAGE, AND HANDLING



A.
Deliver, store, protect, and handle Products to site under provisions of Section 01600.



B.
Accept conduit on site.  Inspect for damage.



C.
Protect conduit from corrosion and entrance of debris by storing above grade.  Provide appropriate covering.



D.
Protect PVC conduit from sunlight.


1.08

PROJECT CONDITIONS



A.
Verify that field measurements are as shown on Drawings.



B.
Verify routing and termination locations of conduit prior to rough‑in.



C.
Conduit routing is shown on Drawings in approximate locations unless dimensioned.  Route as required to complete wiring system.

PART 2 – PRODUCTS


2.01

CONDUIT REQUIREMENTS



A.
Minimum Size: 3/4 inch (19 mm) unless otherwise specified.



B.
Underground Installations:

1. More than Five Feet from Foundation Wall: Use thickwall nonmetallic conduit

2.
Within Five Feet from Foundation Wall: Use plastic coated conduit.




3.
In or Under Slab on Grade: Use rigid steel conduit.




4.
Minimum Size: 3/4 inch (19 mm).



C.
Outdoor Locations, Above Grade: Use aluminum conduit.



D.
In Slab Above Grade:




1.
Use rigid steel conduit.




2.
Maximum Size Conduit in Slab: 3/4 inch for conduits crossing each other.



E.
Wet and Damp Locations:  Use rigid steel conduit.



F.
Dry Locations:




1.
Concealed:  Use rigid and aluminum] conduit, electrical metallic tubing.




2.
Exposed:
Use rigid and aluminum conduit.


2.02

METAL CONDUIT



A.
Rigid Steel Conduit: ANSI C80.1.



B.
Rigid Aluminum Conduit: ANSI C80.5.



C.
Intermediate Metal Conduit (IMC): Rigid steel.



D.
Fittings and Conduit Bodies:
ANSI/NEMA FB 1; material to match conduit.


2.03

PVC COATED METAL CONDUIT



A.
Description:
NEMA RN 1; rigid steel conduit with external PVC 




PVC coating, 40 mil thick.



B.
Fittings and Conduit Bodies:
ANSI/NEMA FB 1; steel fittings with external PVC coating to match conduit.


2.04

FLEXIBLE METAL CONDUIT



A.
Description:  Interlocked steel construction.



B.
Fittings:  ANSI/NEMA FB 1.


2.05

LIQUIDTIGHT FLEXIBLE METAL CONDUIT



A.
Description:
Interlocked aluminum construction with PVC jacket.



B.
Fittings:  ANSI/NEMA FB 1.


2.06

ELECTRICAL METALLIC TUBING (EMT)



A.
Description:  ANSI C80.3; galvanized tubing.



B.
Fittings and Conduit Bodies:
ANSI/NEMA FB 1; steel or malleable iron, compression type.


2.07

NONMETALLIC CONDUIT



A.
Description:  NEMA TC 2; Schedule 40 PVC.



B.
Fittings and Conduit Bodies:  NEMA TC 3.

PART 3 – EXECUTION


3.01
INSTALLATION



A.
Install conduit in accordance with NECA "Standard of Installation."



B.
Install nonmetallic conduit in accordance with manufacturer's instructions.



C.
Arrange supports to prevent misalignment during wiring installation.



D.
Support conduit using coated steel or malleable iron straps, lay‑in adjustable hangers, clevis hangers, and split hangers.



E.
Group related conduits; support using conduit rack. Construct rack using steel channel; provide space on each for 25 percent additional conduits.



F.
Fasten conduit supports to building structure and surfaces under provisions of Section 16190.



G.
Do not support conduit with wire or perforated pipe straps.  Remove wire used for temporary supports



H.
Do not attach conduit to ceiling support wires.



I.
Arrange conduit to maintain headroom and present neat appearance.



J.
Route [exposed] conduit parallel and perpendicular to walls.



K.
Route conduit installed above accessible ceilings parallel and perpendicular to walls.



L.
Route conduit in and under slab from point‑to‑point.



M.
Do not cross conduits in slab.



N.
Maintain adequate clearance between conduit and piping.



O.
Maintain 12 inch (300 mm) clearance between conduit and surfaces with temperatures exceeding 104 degrees F (40 degrees C).



P.
Cut conduit square using saw or pipecutter; de‑burr cut ends.



Q.
Bring conduit to shoulder of fittings; fasten securely.



R.
Join nonmetallic conduit using cement as recommended by manufacturer.  Wipe nonmetallic conduit dry and clean before joining.  Apply full even coat of cement to entire area inserted in fitting.  Allow joint to cure for 20 minutes, minimum.



S.
Use conduit hubs or sealing locknuts to fasten conduit to sheet metal boxes in damp and wet locations and to cast boxes.



T.
Install no more than equivalent of three 90‑degree bends between boxes.  Use conduit bodies to make sharp changes in direction, as around beams.  Use hydraulic one‑shot bender to fabricate bends in metal conduit larger than 2 inch (50 mm) size.



U.
Avoid moisture traps; provide junction box with drain fitting at low points in conduit system.



V.
Provide suitable fittings to accommodate expansion and deflection where conduit crosses, control and expansion joints.



W.
Provide suitable pull string in each empty conduit except sleeves and nipples.



X.
Use suitable caps to protect installed conduit against entrance of dirt and moisture.



Y.
Ground and bond conduit under provisions of Section 16170.



Z.
Identify conduit under provisions of Section 16195.


3.02
INTERFACE WITH OTHER PRODUCTS



A.
Install conduit to preserve fire resistance rating of partitions and other elements, using materials and methods under the provisions of Section 07270.

END OF SECTION

PAGE  
Crosswinds Apartments
16111 - 5
CONDUITError! Main Document Only.

