SECTION 16500

INTERIOR LIGHTING
PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings
B. General provisions of the Contract, including General and Supplementary Conditions
C. Division 01 Specification Sections
D. Section 09900 – Painting
E. Section 16010 – Basic Electrical Requirements

1.2 SUMMARY

A. The work of this section consists of providing labor, materials, tools, appliances and miscellaneous accessories associated with lighting fixture work as indicated herein and on the Drawings and schedules.
1. Interior lighting fixtures, lamps, and ballasts.

2. Emergency lighting units.

3. Exit signs.

4. Lighting fixture supports.

5. Retrofit kits for fluorescent lighting fixtures.

B. Type:  The types of lighting fixtures required for the project include the following:
1. Fluorescent-type fixtures
2. High Intensity Discharge (HID) type fixtures

3. Incandescent type fixtures

C. Applications of lighting fixtures required for project include the following:
1. General interior lighting

2. Supplementary lighting

3. Task lighting

4. Emergency lighting

5. Exterior lighting

1.3 FIXTURES
A. Furnish, assemble, install, and wire up complete, all lighting fixtures including those for general illumination, exit sign, and emergency lighting, and exterior lighting.  Fixtures shall be complete with lamps, lamp holders, and all necessary accessories.  Fixtures shall bear the Underwriters’ Laboratories, Inc. label of approval and be purchased, wired, and installed in accordance with applicable codes.
1.4 EXIT SIGNS AND EMERGENCY LIGHTING SYSTEM
A. Emergency lighting systems shall be a complete and independent system from the general lighting system.  The service shall be as indicated on the Drawings.
PART 2 -  PRODUCTS

2.1 FIXTURES
A. All fixtures shall be as indicated and scheduled on the drawings.  The omission of a type or quantity in the fixtures schedules shown on the drawings will not relieve the Contractor of the responsibility for furnishing all fixtures indicated on the drawings.
B. Provide lighting fixtures, of the size, type, and rating indicted, complete with, but not necessarily limited to, lamps, lampholders, reflectors, ballasts, starters, and wiring.

C. Fixture Types:

1. Fluorescent Fixtures:

a. Provide fluorescent fixtures complete with lamps and ballasts.

b. Provide fluorescent fixtures with G.E. ALF 216 Series lamp sockets, or equal by Leviton, H&H or Bryant.

c. Recess fluorescent fixture lenses, where required, shall be extruded virgin acrylic, prismatic type, minimum 0.125” thick, unless otherwise noted.  For other than lay-in type ceilings, recess fluorescent fixtures shall be flanged type.

d. Fluorescent fixtures in continuous rows shall be supplied with all fixture couplings, chase nipples, and other accessories recommended by the manufacturer for continuous row installation.

2. HID Fixtures:

a. Provide HID fixtures complete with lamps and ballasts.

b. Provide a shield below the lamp to prevent glass, if a lamp breaks, from falling to the floor.

3. Incandescent Fixtures:

a. Provide incandescent fixtures complete with lamps.  Provide recessed incandescent fixtures with trim rings compatible with the ceiling material where fixture is to be installed.

4. Exit Signs:

a. The exit lighting fixtures shall meet the requirements of Feder, State and Local codes.  Exit signs shall have the word “EXIT” printed in red letters at least 6” in height.  The letters and associated arrows shall be of red translucent material place don an opaque background.

2.2 BALLASTS
A. Fluorescent magnetic Type:

1. Fluorescent equipment to have self-contained electronic ballasts “P” rated, CBM-ETL certified, with lowest sound level rating available.  Ballasts to be Advance, Mark V electronic ballast, parallel wired, ballast to match fixture type or Magnatec B series electronic ballast, parallel wired, ballast to match fixture type.
2. Manufacturers:
a. Advance (mark V Style)

b. Magnatec (Electronic)

B. High Intensity Discharge Type:  Ballast for HID lamps shall be high power factor, constant wattage or constant wattage autotransformer, low noise level, a -20°F temperature rating, and shall be furnished by the manufacturer of each type or particular lighting fixture specified.
C. HID lamps shall be clear or coated type as indicated on the drawings and/or as required by the manufacturer of the respective fixtures.
D. Incandescent lamps shall be inside-frosted, 130 volts unless indicated otherwise.
E. All lamps shall be as manufactured by:

1. General Electric Company

2. Philips

3. Sylvania

4. Venture

F. Ballasts for Low-Temperature Environments:

PART 3 -  EXECUTION

3.1 INSTALLATION OF LIGHTING FIXTURES
A. Install lighting fixtures of the types indicated, where shown, and at the indicated heights in accordance with the fixture manufacturer’s written instructions and recognized industry practices to ensure that the fixtures comply with the requirements and serve the intended purposes.  Fixtures shall exactly fit the type of ceiling system scheduled for the space.
B. Provide adequate and safe protection for fixtures and at completion of the work they shall be made clean and free of all foreign material, dust, etc.
C. Furnish and set all inserts, anchors, studs, and hangers for the support of lighting fixtures and respective equipment, and make all necessary adjustments required therein.

D. Verify location and spacing of fixtures with Reflected Ceiling Plans and other reference data before installation.  Coordinate space conditions; including head room clearances, and interferences with ceiling components, such as ducts, opening, beams and piping, prior to installation.

E. In acoustical tile ceilings with concealed mechanical suspension system and in gypboard or plaster ceilings, recessed troffers shall be flanged type fixtures.  In acoustical tile ceilings with exposed mechanical suspension systems, troffers shall be lay-in type.
F. Lamping-Up:  Furnish and install fluorescent, HID and incandescent lamps in all lighting fixtures.

G. Standards:  Comply with NEMA standards, applicable requirements of the NEC pertaining to installation of interior lighting fixtures, and with applicable portions of the NECA’s “Standard of Installation.”

H. Attachment:  Fasten fixtures securely to the indicated structural support members of the building.  Provide separate supports for all recessed ceiling-mounted HID lighting fixtures.  Check to ensure that solid pendant fixtures are plumb.

I. For any type ceiling provide sufficient support for fixtures, either arrange with other subcontractors to strengthen ceiling or support fixtures from structure above independently of ceiling.  Regardless of whether or not the ceiling can support the fixtures, provide securing wires on fixture to structure.  Provide a minimum of two securing wires to 2x4, 2x2, etc.  NOTE:  Securing wires are not the same as support wire.  Securing wires are for prevents a fixture from falling into a space if the ceiling fails under a fire situation.

J. All lay-in fixtures to be connected to grid system with hurricane clips.
K. Fixtures supported by ceiling framing members shall be securely fastened thereto by mechanical means, such as bolts, screws, or rivets.  Clips designed and approved for the purpose shall be permitted.

L. Suspended fluorescent fixtures in continuous rows shall have none stem at the beginning of the row, one stem at each channel joint, and one stem at the end of the row.

M. Fluorescent fixtures mounted individually on stems shall each have two single stem hangers.  Fluorescent fixtures individually surface mounted shall be supported at both ends.

N. Fixtures to be installed in or on painted ceilings and/or walls shall not be installed until painting is completed.  Fixtures installed with paint applied over factory finishes will be rejected.

O. Thermal insulation shall not be installed within 24 inches of the top or within 3 inches of the sides of a recessed fixture enclosure, wiring compartment, or ballast unless labeled for the purpose.  Work of this section includes advising other trades of this requirement so that proper clearances are maintained.
P. Articles 410-13 and 410-76 of the National Electrical Code regarding installation of lighting fixtures in combustible ceilings or walls shall apply.

3.2 ADJUST AND CLEAN

A. Clean interior lighting fixtures of dirt and debris upon completion of installation.

B. Protect installed fixtures from damage during remainder of construction period.

3.3 FIELD QUALITY CONTROL

A. Upon completion of installation of lighting fixtures, and after building circuitry has been energized, apply electrical energy to demonstrate capability and compliance with requirements.  Where possible, correct malfunctioning units at site, then retest to demonstrate compliance; otherwise, remove and replace with new units, and proceed with retesting.

B. Replace defective and burned out lamps for period of 6 months following the date of Substantial Completion of that phase.

C. At the date of Substantial Completion, replace lamps in interior lighting fixtures which are observed to be noticeably dimmed after Contractor’s use and testing, as judged by Architect.  Furnish stock or replacement lamps amounting to 15% (but not less than one lamp in each case) of each type and size lamp used in each type fixture.  Deliver replacement stock as direct to Owner’s storage space.

D. Refer to Division-1 sections for the replacement/restoration of lamps in interior lighting fixtures, where used for temporary lighting prior to the date of Substantial Completion.

E. Test for Emergency Lighting:  Interrupt power supply to demonstrate proper operation.  Verify transfer from normal power to battery and retransfer to normal.

F. Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results.  If adjustments are made to lighting system, retest to demonstrate compliance with standards.

3.4 GROUNDING

A. Provide tight equipment grounding connections for each interior lighting fixture installation where indicated.

END OF SECTION

Crosswinds Apartments
16500 - 5
INTERIOR LIGHTING

