
SECTION 16510PRIVATE 


INTERIOR LUMINAIRES

1 PART 1   GENERAL


1.01

SECTION INCLUDES



A.
Interior luminaries and accessories.



B.
Emergency lighting units.



C.
Exit signs.



D.
Ballasts.



E.
Fluorescent lamp emergency power supply.



F.
Lamps.



G.
Luminaries accessories.



1.02
seq level2 \h \r0 
RELATED SECTIONS




Not Used


1.03
seq level2 \h \r0 
REFERENCES



A.
ANSI C78.379 ‑ Electric Lamps ‑ Incandescent and High-Intensity Discharge Reflector Lamps ‑ Classification of Beam Patterns.



B.
ANSI C82.1 – Ballasts for Fluorescent Lamps ‑ Specifications.



C.
ANSI C82.4 ‑ Ballasts for High‑Intensity Discharge and Low Pressure Sodium Lamps (Multiple Supply Type).



D.
ANSI/NFPA 70 ‑ National Electrical Code.



E.
ANSI/NFPA 101 ‑ Life Safety Code.



F.
NEMA WD 6 ‑ Wiring Devices‑Dimensional Requirements.



G.
Reference to General Conditions.


1.04
seq level2 \h \r0 
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Shop Drawings: Indicate dimensions and components for each luminaries that is not a standard product of the manufacturer.



C.
Product Data: Provide dimensions, ratings, and performance data.



D.
Manufacturer's Instructions:
Indicate application conditions and limitations of use stipulated by product testing agency specified under Regulatory Requirements.



E.
Manufacturer's Instructions:
Include instructions for storage, handling, protection, examination, preparation, and installation of product.


1.05

seq level2 \h \r0 

PROJECT RECORD DOCUMENTS



A.
Submit under provisions of Section 01700.



B.
Accurately record actual locations of each luminary.


1.06

seq level2 \h \r0 

OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data: Include replacement parts list.


1.07

seq level2 \h \r0 

QUALIFICATIONS



A.
Manufacturer:  Company specializing in manufacturing products specified in this Section with minimum three years documented experience.


1.08

seq level2 \h \r0 

REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Conform to requirements of NFPA 101.



C.
Furnish products listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and shown.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2   PRODUCTS


2.01

LUMINAIRES



A.
Furnish products as specified on Drawings.



B.
Manufacturers: (See Schedule on drawings)



C.
Description:

Recessed Troffer type luminaries with ballast, lamps and reflectors installed in fixture by luminaries manufacturer.



D.
Size:
2’ x 4.



E.
Material:
Sheet size housing.



F.
Enclosure:
Prismatic acrylic lens, pattern 12.  Provide gasketing between enclosure and frame and between frame and luminaire housing.



G.
Photometric Control Elements:
Specular Aluminum reflector warranted for 25 years.



H.
Photometric Performance:
Minimum coefficient of utilization 0.65 at room cavity ratio of 2 with ceiling wall-floor reflectance of 70-50-20 percent.



I.
Installation Conditions:
Normal



J.
Mounting:
recessed in grid ceiling.



K.
Ballast:

Provide minimum 5-year warranty.



L.
Provide Emergency Units with battery pack and charger.


2.02
seq level2 \h \r0 

seq level3 \h \r0 
EXIT SIGNS



A.
Manufacturers:
See Schedule on drawings.






B.seq level3 \h \r0 
Description:
Exit sign fixture.



C.
Housing:  Extruded aluminum.



D.
Face:  Translucent plastic face with red letters on white background.



E.
Directional Arrows:  Universal type for field adjustment.



F.
Mounting:  Wall.



G.
Battery:

12 volt, nickel‑cadmium type, with 1.5-hour capacity.



H.
Battery Charger:
Dual‑rate type, with sufficient capacity to recharge discharged battery to full charge within twelve hours.



I.
Lamps:
Manufacturers standard.



J.
Input Voltage:
120 volts.


2.0seq level2 \h \r0 3

BALLASTS



A.
Fluorescent Ballast (New Fixtures):




1.
Description:

ANSI C82-1. High power factor type electromagnetic ballast, CBM certified.

2. Provide ballast suitable for lamps specified.

3. Voltage:

120 volts.

4. Source Quality Control:
Certify ballast design and construction by Certified Ballast Manufacturers, Inc.

 2.04

LAMPS



A.
Fluorescent Lamp Manufacturers (New Fixtures):


1. Panasonic Tricolor F40EX50 (T10).

2. Phillips Initial Lumens 3550.

3. Rated Average Life 20,000 HRS.

4. Substitutions:
Under provisions of Section 01600.

3

seq level1 \h \r0 

seq level2 \h \r0 

seq level3 \h \r0  PART 3   EXECUTION


3.01

EXAMINATION



A.
Examine substrate and supporting grids for luminaries.



B.
Examine each luminaire to determine suitability for lamps specified.


3.02

seq level2 \h \r0 

INSTALLATION



A.
Install in accordance with manufacturers instructions.



B.
Locate recessed ceiling luminaries as indicated on reflected ceiling plan.



C.
Install surface mounted luminaries and exit signs plumb and adjust to align with building lines and with each other.  Secure to prohibit movement.



D.
Re-hang existing 277-volt fixtures as indicated on 


3.03
seq level2 \h \r0 
FIELD QUALITY CONTROL

seq level2 \h \r0 


A.
Operate each luminaire after installation and connection. Inspect for proper connection and operation.


3.04seq level2 \h \r0 

ADJUSTING



A.
Aim and adjust luminaries as directed.



B.
Adjust exit sign directional arrows as indicated.



C.
Re-lamp luminaries that have failed lamps at Substantial Completion.



3.05
seq level2 \h \r0 
CLEANING



A.
Clean Work under provisions of Section 01700.



B.
Clean electrical parts to remove conductive and deleterious materials.



C.
Remove dirt and debris from enclosure.



D.
Clean photometric control surfaces as recommended by manufacturer.



E.
Clean finishes and touch up damage.


3.06
seq level2 \h \r0 
DEMONSTRATION



A.
Provide systems demonstration under provisions of Section 01650.



B.
Provide minimum of two hours demonstration of luminaire operation.


END OF SECTION

PAGE  
Crosswinds Apartments
16510 - 1
INTERIOR LUMINAIRES

