Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

June 21, 2005

Mr. Kirk Pichon

Department of Building Safety

2056 Second Street

Slidell, La 70458

RE:  
Christian Community Church


Location: 1460 W. Lindburg Dr.

Dear Mr. Pichon, 

The A-1 drawing shows locations where a 1-hour fire partition is required on the 1st floor; please find GA File No. WP 3514 attached to describe how the 1-hour rating will be constructed.  Parts of the floor on the second floor also must be 1-hour rated, as they form the ceiling of the 1-hour rated areas on the 1st floor.  Please find GA File No. FC 5406 attached to describe how the 1-hour floor rating will be constructed.

The A-2 drawing shows  “Building Section ‘B’ at Kitchen” and “Building Section ‘C’”, these sections are being revised to remove the “metal decking pan” under the ¾” plywood subfloor, as the metal decking pan is not a requirement for 1 hr rated floor.  

Sincerely,

David Dammon

Project Manager

cc: John Wickert, Christian Community Church

