Sizing Grease Interceptor for Community Christian Church

Ea. Bowl

W x L x D

18 x 18 x 14 x 3 = 13,608 cu in.

Capacity

1 gal = 231 cu in

13,608/231 = 58.9 gal

Drainage Load normally at 75% capacity

58.9 x 75% = 44.18 gal

Flow Rate = Actual Drainage Load / Drainage Period

1 minute flow rate is 44.18 / 1 = 44.18 gal/min

2 minute flow rate is 44.18 / 2 = 22.09 gal/min

Grease Interceptor at 1 minute flow rate is equal to 100 pound Interceptor with a 50 gal/min flow control device

Grease Interceptor at 2 minute flow rate is equal to 50 pound Interceptor with a 25 gal/min flow control device

St Tammany Health Dept does not require any given flow rate.  Recommendation is to have a flow control device at 25 gal/min and use a 70 lb interceptor.

