[image: image1.jpg]







Date of letter: 7/3/2007
Commercial Third-Party Plan Review Letter






PLAN REVIEW CORRECTION NOTICE
SECTION 1: ARCHITECTURAL AND STRUCTURAL REVIEW

	CODE SECTION
	DESCRIPTION OF VIOLATION

	IBC 106 AND IBC 1603
	PLEASE PROVIDE THE METAL BUILDING PACKAGE WITH CALCULATIONS SEALED BY BTHE ENGINEER OF NRECORDS. PLEASE PROVIDE FOUNDATION CALCULATIONS.

	IBC 1704
	PLEASE NOTE THAT SPECIAL INSPECTIONS WILL BE REQUIRED. PROVIDE STATEMENT OF SPECIAL INSPECTIONS AND SPECIAL MINSPECTOR HIRED FOR THE PROJECT

	IBC 903.2.1.3.
	PLEASE NOTE THAT AN  NFPA 13 SYSTEM SHALL BE REQUIRED SINCE THE OCCUPANT LOAD EXCEEDS 300

	IBC TABLE 503.3

IBC 506 AND IBC 705
	ALLOWABLE AREA ARE EXCEEDED. A-3 BEING MOST RESTRIVE OCCUPANCY ALLOWS ONLY 9500 SF PER FLOOR. THE EXISTING SACTUARY, THE EXISTING FELLOWSHIP HALL AND THE NEW FELLOWSHIP HALL TOTAL OVER 25000SF.

PLEASE CLARIFY IF AREA MODIFICATIONS OF IBC 506 APPLY. (FRONTAGE AND/OR SPRINKLER).

ALSO, IF THE NEW FELLOWSHIP SHALL IS SEPARATED BY A 3 HOUR FIRE WALL IN ACCORDANCE WITH IBC TABLE 705.4, ALLOWABLE AREAS WOULD BE OK. PLEASE NOTE THAT THIS WOULD MEAN INSTALLING 3-HR FIRE DOORS(IBC TABLE 715.4) ON THE FIRE WALL WHERE OPENINGS OCCUR. PLANS INDICATE ONE HOUR WALL. ALL REQUIREMENTS OF 705 FOR FIR WALLS SHALL BE MET IF THAT OPTION IS SELECTED.

	IBC 705 AND IBC 706
	PROVIDE UL ASSEMBLY DETAILS FOR ALL FIRE BARRIERS AND FIRE WALLS NOT CURRENTLY SHOWN ON THE PLAN. ALSO NOTE THAT A 2HR FIRE BARRIER IS REQUIRED. PLANS INDICATE ONE HOUR. REVISE PLANS.

	IBC 1004

IBC 1004.3
	PLEASE PROVIDE TOTAL OCCUPANT LOAD OF THE ASSEMBLY AREA. ALSO CLARIFY IF SEAT ARE FIXED OR LOOSE IN THE FELLOWSHIP HALL.

OCCUPANT LOAD OF THE A-3 SHALL BE POSTED. IT APPEARS TO BE OVER 750 PEOPLE. PLEASE SHOW ON DRAWINGS. SHALL BE FIELD INSPECTED.

	IBC 907.2.1.


	PROVIDE FIRE ALARM AND SPRINKLER  DRAWINGS . THIS MAY BE A DEFFERED SUBMITTAL. PROVIDE PRIOR TO INSTALL.


SECTION 2: MECHANICAL,  ELECTRICAL AND PLUMBING REVIEW
Approved. 7/3/2007.


GENERAL NOTES:

The following comments based on the uniform construction codes as adopted by the State of Louisiana shall be resolved before a permit is issued. Life safety review is performed by the State Fire Marshall. This correction list is not a building permit. The approval of plans and specifications does not permit the violation of any federal, state or local regulations
Note: Please provide a written response narrative detailing how each comment was addressed.  Failure to provide a response   may result in both delay of the review and rejection of the revised plans.  Note that responses such as “Will  Comply” do not constitute a complete response. All Comments must be addressed on the drawings unless other wise noted.

PROJECT INFORMATION





Project Name:�������������������� Bens Ford Christian Church





Permit Number: WP07228





Job address:59226  Mt. Pleasant Rd, Bogalusa, LA 70427


Use of building: Church-Fellowship hall





Construction type: III-B�


Occupancy type: A-3/E





Number of stories 2 Number of units N/A





Square footage: 9500SF per floor.





Plans reviewer: John Chumba, CBO, MCP





State Fire Marshall review complete? YES





State Fire Marshall’s project number: 329384





Scope of project: New two storey Fellowship hall on first floor and classrooms on the upper floor.





STATUS OF REVIEW





( Approved





(Rejected





( Approved with conditions-letter





TIME LINES





Date of submittal: 7/2/2007





Review date: 7/3/2007





Due date: 7/9/2007. Reviewed on time.








CONTRACTOR INFORMATION





Name: Saucier  Builder L.L.





Business address: 80215 Watts Thomas Rd. Bush, La. 70431  





Phone contact: 985-





Fax contact





Email contact:














DESIGNERS  INFORMATION





Name:Edward Gremillion





Address:1095 Florida avenue, Slidell, LA, 70458





Phone contact:985-649-5832





Fax contact: 985-649-5832





Email contact:petedammon@yahoo.com




















ADOPTED CODES:





Applicable Codes as per state law: IRC 2006, IBC 2006, IFGC 2006, IEBC 2006, LSPC 2000, NEC 2005, IMC 2006














OTHER NOTES:





ONCE METAL BUILDING PACKAGE IS SUBMITTED TO ENGINEER FOR LIVE, DEAD, WIND LOAD CALCULATION TO DETERMINE FOUNDATION/FOOTINGS, THE FOUNDATION MAY BE POURED AFTER INSPECTION APPROVAL.





ALL COMMENTS AS PER THE STATE FIRE MARSHALLS LETTER SHALL BE ADDRESSEED DURING INSPECTIONS.








