Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

October 25, 2007

Mr. Jim Waite

Office of State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA 70806

RE:  
P0333770


Aldersgate United Methodist Church


360 Robert Road


Slidell, LA  70458-0000

Dear Mr. Waite,

With regard to the above referenced project, a supervised automatic sprinkler system has been added to cover the entire building.  The sprinkler system negates the need for a 2-hour fire-area separation as well as a 1-hour rated corridor in the Business area.  The fire rated walls will be reduced to smoke partitions.  Since the sprinkler system has been added the area of refugee requirement has been eliminated as well.   A sprinkler riser has been added to the General Purpose Equipment Room.

If you have any questions, please feel free to call.

Sincerely,

David Dammon

Project Manager

