
STATE OF LOUISIANA

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement and Building Safety

8181 Independence Boulevard

Baton Rouge, Louisiana 70806

225-925-4920

H “BUTCH” BROWNING

FIRE MARSHAL

I N F O R M A T I O N  R E Q U E S T

N O T   -   F O R   -   P E R M I T T I N G

	ROBERT WILTSE, ARCHITECT

DAMMON ENGINEERING INC

1095 FLORIDA AVE

SLIDELL, LA  70458-0000
	RE:  P0368920

NORTHSHORE CHURCH

300 KENSINGTON AVE

SLIDELL, LA  70458-0000

NFPA 101, 2006

ASSEMBLY OVER 300 OCCUPANTS




Dear Applicant:

Additional information is required to perform a proper review.  The project referenced above is being held pending submission of the following information:

1.
RS 40:1574 and/or RS 40:1730.39.A  Additional drawings and/or specifications are required:

a. a)  101:9.6.3.6.1  The general evacuation alarm signal shall operate throughout the building.  Portions of the building marked N.I.C." on the shop drawings shal be included as part of the scope of work.  Revise shop drawings to include device loctions for ALL portions of the building. 

b. b)  Provide documentation to substantiate compatibility between additional required devices and the control panel.  Provide copies of the listings in the "Fire Protection Equipment Directory" or printouts of the listings on the website at www.ul.com for the devices.

c. c)  NFPA 72:4.4.1.5  Revise battery calculations to incorporate changes in appliance demands and provide batteries with sufficient capacity to accommodate the revised loads.

NOTE: Shop drawings shall reflect the floor plan of the reviewed and approved architectural drawings. Changes to construction which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review.   

Due to the lack of information, the referenced project has NOT been reviewed.  Please direct the requested information to my attention.  Processing will continue upon receipt of the information requested above.  Enclose a copy of this letter with future submittals and/or other correspondence pertaining to this project.

This project will be returned as "NOT IN COMPLIANCE" if the requested information is not received by this office within 21 days of the date of this letter, thereby requiring a RESUBMITTAL of the entire project along with a new completed application and appropriate review fee.

CONSTRUCTION IS NOT AUTHORIZED until a satisfactory review has been performed and a formal review letter has been issued by this office.

REVIEWED BY:

LAWRENCE DELAUNE

ARCHITECT SUPERVISOR

CC:

Northshore Church

Simplex Grinnell

Property Insurance Association*

St Tammany Fire Protection District No 1*

City Of Slidell*

New Orleans District*     5042194600

Aug 14, 2009

P0368920 - PAGE 2

