The Free Church of The Annunciation


Architect: Bob Sollberger   643-4369

Contractor: RHL Construction   Renee C504:338-7209

Electrician: Blanco Electric 504-885-5246

Scope:

Basement flooded during hurricane. All A/C air handler, boiler, water heater, pumps electrical panels, disconnects and conduits were under water.

There was approximately one foot of water in the halls and sanctuary, only the sanctuary had water over the surface mounted wire ways and receptacles. New electric A/C units will replace existing chiller.

Demolition:

Remove and scrap two single-phase electrical panels, two three phase disconnects, and a junction box. Remove conduit and wire back to the water line and prepare to tie the circuits into a junction box. Remove a 16 Ckt 100 amp single-phase panel on the second floor. Remove the wire mold and damaged receptacles in the sanctuary.

Reconstruction:

Install one 400A three-phase panel and one 200A single-phase panel in a closet located in room 106. A new service will be installed on the backside of the building to feed the 3-phase panel. 

A new panel will be installed in the hall of the second floor replacing an existing one.

Eight all electric 5 Ton A/C units will be installed in various locations.

Install the wire mold and receptacles in the sanctuary.

