
STATE OF LOUISIANA

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard

Baton Rouge, Louisiana  70806

225-925-4920

HENRY H. FRY

DEPUTY ASSISTANT SECRETARY

NEW CONSTRUCTION

EDWARD GREMILLION

DAMMON ENGINEERING, INC

1095 FLORIDA AVE

SLIDELL, LA  70458-0000
RE:  P0287103

STARC ADULT CARE

VIOLA ST

MANDEVILLE, LA  70448

NFPA 101, 2003

DAY CARE CENTER OVER 13 CAP.

Dear Applicant:

This is to advise that we have reviewed the drawings and specifications for the subject proposed construction and have determined that they appear to satisfactorily comply with the adopted laws, codes, rules and regulations of The State Fire Marshal subject to the following requirements:

NOTE:  THE COMMENTS LISTED BELOW IDENTIFY APPARENT DEFICIENCIES DETECTED IN OUR REVIEW OF THE DOCUMENTS SUBMITTED.

1.
101:16.2.9 Provide emergency lighting according to NFPA 101:7.9 including exit discharge (exterior). 

2.
101:16.3.2  Separate UTILITY from other parts of the building by 1 hour fire resistive construction with self-closing 45 minute labeled door/frame assembly or provide automatic sprinkler protection in accordance with Section 9.7 and smoke partitions with self-closing doors in accordance with 8.7.1.2 and 8.4. (Sprinkler piping for isolated hazardous areas connected to domestic water supply shall comply with 101:9.7.1.2). 

3.
101:16.3.4  Provide a fire alarm system in accordance with 101:9.6.  In facilities required to be fully accessible, alarm notification shall be by both audible and visual means in accordance with NFPA 72. 

______________________________________________________________________________________

NOTE:  THE FOLLOWING COMMENTS IDENTIFY ISSUES FOR INFORMATIONAL AND CAUTIONARY PURPOSES OR ISSUES THAT COULD NOT BE VERIFIED IN THE SUBMITTED DOCUMENTS.

4.
LRS 40:1711  Provide safety glazing in hazardous locations. 

5.
LRS 40:1651  Submit fire alarm system shop drawings with plan review application and fee prior to installation of any work of this section.  Such work shall not commence until shop drawings have been found to be in compliance with applicable codes by this office.  The submittal shall include a copy of this letter and shall be in accordance with the submittal requirements outlined in the memorandum dated June 24, 1993 which was distributed from this office to all state licensed fire alarm contractors, architects and engineers.  Specify the "Type of Signaling System" to be utilized, identify the monitoring station, describe the evacuation system ("zoned" or "general"), and include information concerning the means of protecting fire command centers, circuitry, and other essential equipment, such as may be required for high-rise buildings, as applicable. 

6.
Shop drawings for fire protection systems, such as Fire Alarm, Sprinklers, and Suppression Systems, that are required to be submitted to this office for review, shall be routed through the "Professional of Record's" (Architect / Engineer) office, and shall be stamped with his "Shop Drawing Review Stamp" or equivalent, indicating that shop drawings have been reviewed by him for conformance with plans, specifications, and appropriate codes. 

7.
LRS 40:1653 and 40:1628  All work and inspections of fire alarm, fire suppression, automatic sprinkler and fire extinguishing systems or portable fire extinguishers shall be performed by a State of Louisiana certified agent. 

8.
101:7.2.1.5.9  Doors shall be openable with ONLY one releasing operation.  A two-step release, such as a knob and an independent slide bolt, is NOT acceptable. 

9.
101:16.2.2.2.5  Bath room door locks shall permit opening from the outside in an emergency.  The opening device shall be readily accessible to the staff. 

10.
101:16.2.11.1.1  Operable windows for rescue assistants shall provide a clear opening of not less than 20" wide by 41" high, or 34.2" wide by 24" high.  The bottom of the opening shall be not more than 44" above the floor. 

11.
ADA-AG 4.1.3(9) and 4.3.10  Each required exit shall be an accessible means of egress. 

12.
10:5.1.4  Provide portable fire extinguishers within the following travel distances (See Tables 10:5.2.1 and 5.3.1);

a)  Travel distance to a fire extinguisher shall not exceed 75 feet for Class A, C and D fires.

b)  Travel distance to a fire extinguisher shall not exceed 50 feet for Class B fires (liquids).

13.
NFPA 10:1.5.10  Top of fire extinguisher, having a gross weight less than 40 lb, shall be not more than 5 feet above the floor; 3-1/2 feet if gross weight 40 lbs or greater. 

14.
HVAC system shall be constructed in accordance with 101:9.2. 

15.
LRS 40:1730.25  The documentation provided for the subject facility appears to comply with The Commercial Building Energy Conservation Code based on ASHRAE/IES 90.1-1989 (Energy Code). 

16.
NOTE: Please enclose a copy of this letter with future submittals or other correspondence pertaining to this project. 

Changes to construction in the field which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review prior to final inspection.  If an Architect or Civil Engineer is not required by RS 37:155, revisions shall be submitted by the Owner.  Submittals shall include plans, completed application, a minimum $55.00 review fee, and a copy of the most current plan review letter.

Compliance with code requirements for fire protection systems, such as Fire Alarm, Sprinkler and Suppression Systems, is determined by separate shop drawing submittal and is not included in this review.

This review shall in no way permit and/or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

This review is valid for 180 days from the date of this letter.  Construction permits must be issued and/or construction must commence within this time period.

This office requires certification of the completed project in accordance with the approved documents (certificate enclosed).

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below two (2) to three (3) weeks in advance.  The plans stamped reviewed by this office must be available on job site at time of inspection.  Certificate of completion must be provided to the inspecting Deputy for final inspection.

REVIEWED BY:

OTIS RAMKE

ARCHITECT

CC:

Starc

Healthcare District*     2259254270

Wayne Berggren*

Jan 28, 2005

P0287103 - PAGE 1

