Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

March 20, 2006

Mr. Kenneth Robichaux

Office of State Fire Marshal 

Department of Public Safety and Corrections

8181 Independence Boulevard

Baton Rouge, Louisiana 70806

RE: Bus Group PO300672


Dear Mr. Robichaux,

With regard to the above referenced project, we are addressing the issue regarding the Fire Marshal letter dated Nov. 10 2005 (copy attached), line item #5. Enclosed please find a Mezzanine Plan drawing showing the accurate travel path distance.

In the front of the building, the roofline is higher in that area of the showroom, therefore there is no access.  With a travel distance starting 3’ from the corner and going to the stairs, there is a total travel distance of 44’-4 ½”.  Also, I have added two smoke detectors and some emergency lighting.  All the other items have been addressed.  We are asking for an approval for this mezzanine plan.  

Thank you for your help with this matter.  Please call me with any questions you may have.

Sincerely,

Chuck Dammon

VP/Project Manager

Attachments:
Fire Marshal Letter



Fire Marshal Drawing, Indicating Markup



New Mezzanine Plan with Travel Distance
