Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

October 13, 2005

Ms. Linda Burch

Office of State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA 70806

RE:  
P0299640  MAURIN WAREHOUSE

Dear Ms. Burch,

With regard to the above referenced project, please note that we have revised the plans to make the 1-hour fire rating around the office build-out as optional.  The existing warehouse is 20,000 sf and the office build-out is 1200 sf.  NFPA 101 para. 6.1.14.1.3 (3) states that accessory occupancies shall not be required to be separated from the primary occupancy when the administrative or other office rooms are not more than 25% of the principal occupancy.  

Sincerely,

David Dammon

Project Manager

