Roof Inspection for HAS

Tuesday, May 13, 2008

Today, after literally weeks of calling Associated Contractors a roofer from QUALITY

EXTERIOR SERVICES contacted me regarding the leak at the HAS building.  The name of their project manager is TONY TORRES. 

We met at the building and he inspected the roof, took photos, and then informed me that his company was not the roofer on this job, but they do work for Associated and were asked to inspect the roof for problems.

Mr. Torres showed me several photos and explained that there are several flaws in the installation of this roof.  There are screws where there should be none, many rivets missing along the length of almost all the sections of metal.  In general, he stated that the roof was incorrectly installed and the small leaks will become large ones over a short period of time.

He also stated that had the roof been installed properly, the material manufacturer should have given HAS a warranty on the product, but he is sure there is not one because of the incorrect way the roof was installed.

An additional condition he mentioned is the remains of metal shavings lying on the metal surface of the sheets that are rusting and beginning to adhere to the painted surface.  He stated that this would ultimately cause the metal sheets to begin rusting also. Mr. Torres indicated that his report will be presented to his manager tomorrow Wednesday and will be forwarded to Associated.  We should contact Associated if we want a copy of the report

Follow up

Wednesday, May 28, 2008

Have had two meetings with Charles Brigham, owner of Brigham Roofing, the company that installed this roof.

First meeting was on 5/13/08.  He did not have a stepladder to check inside, but he did check the roof from outside and stated that he did not see any problems from outside.  He agreed to come back next week with a stepladder so we could inspect the underside of the roof for signs of problems.

We met again on Tuesday, May 27.  Mr. Brigham began looking above the ceiling tiles for problems.  What he found was failures in properly installing the air conditioning ducts especially where flexible ducts are fastened to the larger ridged ductwork.

Sealing tape is not applied well, flanges are not fastened to larger ducts, and flexible ducts are not tightly fastened to the flanges. Moisture is present at several fittings.  This condition appears to be the source of water stains on several ceiling tiles.

I have notified Associated Contractors of this condition and also contacted Mega Air and asked that they meet with me at the HAS building as soon as possible. Am now awaiting a call back from Mega Air.

