DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

December 4, 2009

To: 
Mr. David Jones

REF: PO371441 


Honaker Funeral Home


New Crematory


Slidell, LA

Dear Mr. Jones,

Please see the below list of responses to your “Information Request” letter dated Oct 27, 2009. 

1. No response.

2. Modifications have been made to the plans to reflect the requirements of NFPA 82, and NFPA 54.

3. Please see the attached documents from the Incinerator manufacturer. I have also attached the UL listing for this product, and a sheet listing the standards used for UL testing of Incinerators. (This piece of equipment has been tested by UL against the requirements of NFPA 82 and NFPA 54)

4. Repeat response from #3.

5. UL tested clearances are listed as 1” to combustible from sides, 18” from top, 30” from back, and 4” from chimney sections. These clearances are maintained.

6. Increased wall separating the Incinerator room from the rest of the building to a 2hr rated firewall that will demise to roof deck. GA file no WP 4135. (A detail for this wall is on sheet A-1)

7. Coversheet Information:

a) Design Loads added to Coversheet.

b) 1. Roof Live Load =  20 psf uniform, 300lb concentrated

2. Roof Snow Load  = 0 psf

c) Wind pressure = 33.6 psf

d) Simplified Method (1) used.

Structural Framing Information

a) See MWFRS NOTES on sheet A-2.

b) Shown on Coversheet.

Exterior Elevation Information

a) See Opening protection notes on Sheet A-5 and A-6.

b) Maximum spacing for fastening all components subject to wind, are listed in the tables provided on sheet A-7.

c) Note added to A2 & A3 Identifying C.J. as Lateral Bracing.

Building and Wall Sections

a) Graphic and notes added to sheets A2 & A3.

b) Repeat response from Ext. Elev. Info. (b).

Fuel Gas Information

a) Note and dimension added to sheet A-3 showing clearance to combustibles.

b) Note and dimension added to sheet A-3 showing chimney size. Note added for 3-tier hot air stack with internal air spaces.

c) All penetrations through the 2hr. fire-rated wall assembly shall be sealed with a UL listed Fire caulk. Note added to sheet A-1.

NOTE: 

In regards to Fire Protection:

I have added the requirement of a Fire suppression system in the area of the Incinerator to 
satisfy the requirements of NFPA 82: 4.2.7.3. The specifications for this system will be submitted by others.

Sincerely,

Brandon Nowakowski

Dammon Engineering
Attachments:

1. RFI letter dated Oct 27, 2009. (4 pages)

2. Documents from UL listing. (3 pages)

3. Incinerator mfg. Product Literature and Installation Manual. (15 pages)

4. Revised Drawings. (Coversheet, A1, A2, A3, A5, A6, A7)
