554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net

April    2014

Ms. Wendy Ferrill, B.E.

c/o Mississippi State Department of Health

570 East Woodrow Wilson

Jackson, MS 39215-1700

Re: 	Dreamland Mobile Home Park, Nicholson Water Association,

PWS_ID# 0550041, Pearl River County, Ref #116069

Dear Ms. Ferrill,

In reply to the items requested in your correspondence of April 8, 2014, the following information is presented for your consideration.  Please be aware that the Dreamland Mobile Home Park is an existing Mobile Home Park and the plans and specifications are for rehabilitation and upgrade of the current water and wastewater facilities.

- We contacted the Mississippi DEQ.  At this point we have been informed that due to the fact that the Dreamland Mobile Home Park is an existing park, and that the Dreamland Mobile Home Park wastewater collection system has recently proposed to interconnect to an existing public permitted wastewater treatment facility (the Nicholson Sewerage District) that a submittal to the MDEQ is not required.

- We have contacted the Nicholson Water and Sewage Board, and at this point have a verbal agreement allowing Dreamland to interconnect their water and sewer with the District.  I have requested a formal declaration that I shall forward to you upon receipt.

- See reply item # 2.

- Water mains and sewer mains shall be separated by 10’ horizontally and 18” vertically (water above sewer) when crossing.  This information shall and has been incorporated into the design plans and specifications sheets.

- As discussed with the Nicholson Water Association, water samples shall be collected and submitted to the Mississippi State Department of Health for analysis and approval.   Disinfection shall be using a 50 mg/l free chlorine residual for a contact time for 24 hours.

- A title page shall be provided.

- The Dreamland Mobile Home Park exists, therefore, there are no “proposed” sites; however, we shall delineate the lot sites on the Dreamland Upgrade/Modification plans sheets.

Should you have any questions, or if further information if required, please feel free to contact me.

Respectfully,

Brian A. Mistich, P.E.

Mississippi Registration #20971