DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


554 Old Spanish Trail


                 P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

August 24, 2011
To: 
Hunter Charbonnet

Casey Civil, LLC

1080 Old Spanish Trail, Ste.8


Slidell, LA 70458

REF: Owens & Minor Tenant Buildout, Opening Reinforcement Design


2700 Brittmore Rd.


Houston, TX 77043

Dear Mr. Charbonnet,

We have received the plans and details on the existing concrete wall panels. Based on the new available information:
1. Precast panels are +/- 20’-0” wide.

2. Reinforcement consists:

· Vertical: #4 12” o.c. (each face)

· Horizontal: #4 15” o.c. (each face)

3. Concrete compressive strength = 3,000 psi @ 28 days

Considering the substantial steel reinforcement and panel width, no steel lintel will be required. Once the opening has been cut, please verify that the reinforcing steel that is called out on the plans was actually installed in the precast panels.

   Sincerely,

Emmett G. Dammon, P.E.

Dammon Engineering

