SECTION 14 21 00

ELECTRIC TRACTION ELEVATORS
PART 1 GENERAL

1.01 SECTION INCLUDES

A. Electric Traction elevators.


1.02 RELATED SECTIONS

(Specifier Note:  ADD/DELETE/MODIFY the Section Numbers and Titles to correspond with specific project requirements)

A. Section 01 50 00 – Temporary Facilities and Controls

B. Section 03 30 00 – Cast-in-Place Concrete:

C. Section 04 20 00 – Unit Masonry

D. Section 05 50 00 – Metal Fabrications

E. Section 07 16 00 – Cementitious Waterproofing

F. Section 23 00 00 – Heating, Ventilating, and Air Conditioning

G. Section 26 00 00 – Electrical

H. Section 26 30 00 – Electric Power Generating and Storing Equipment

I. Section 27 30 00 – Voice Communications

J. Section 28 31 00 – Fire Detection and Alarm

K. Section 31 00 00 – Earthwork

1.03 REFERENCES

A. Industry and government standards referenced include the following:

1. ICC/ANSI A117.1 Accessible and Usable Buildings and Facilities

2. ADAAG – Accessibility Guidelines for Buildings and Facilities

3. ANSI/NFPA 70, National Electrical Code

4. ANSI/NFPA 80, Standard for Fire Doors and Fire Windows

5. ASME/ANSI A17.1, Safety Code for Elevators and Escalators.

1.04 PERFORMANCE REQUIREMENTS

A. Car Performance

1. Car Speed ± 5% of contract speed under any loading condition or direction of travel.

2. Car Capacity:  Safely lower, stop and hold (per code) up to 125% of rated load.

B. System Performance

1. Vertical Vibration (maximum): 25 mg

2. Horizontal Vibration (maximum): 25 mg

3. Jerk Rate (maximum): 4.0 ft/sec3
4. Acceleration (maximum) 1.5 ft/sec2
5. In Car Noise: ≤ 55 dB(A)

6. Leveling Accuracy: ±0.2 inches

7. Starts per hour (maximum):  80

1.05 SUBMITTALS

(Specifier Note:  ADD/DELETE/MODIFY the Section Numbers and Titles to correspond with specific project requirements)
A. Conform to requirements of Section 01 33 00 Submittal Procedures and Section 01 78 00 Closeout Submittals

B. Product Data:  Submit manufacturer’s product literature for each proposed system.  

1. Cab design, dimension and layout

2. Layout, finishes, and accessories and available options.

3. System capacity and performance.

4. Controls, signals and operating system.

5. Color selection charts for cab and entrances.

C. Shop Drawings: 

1. Clearances and travel of car,

2. Clear inside hoistway and pit dimensions.

3. Location and layout of equipment and Signals 

4. Car, guide rails, buffers and other components in hoistway.

5. Maximum rail bracket spacing.

6. Maximum loads imposed on building structure.

7. Hoist beam requirements

8. Location and sizes of access doors

9. Location and details of hoistway door and frames

10. Electrical characteristics and connection requirements

D. Closeout Submittals:  

1.
Manufacturer's operation and maintenance manuals.

2. Inspection Certificates and Permits.

1.06 QUALITY ASSURANCE

A. Manufacturer: Shall have a minimum of 10 years experience in the fabrication, installation and service of elevators. Manufacturer shall be ISO 9001 certified, and have a documented quality assurance program.

B. Installer:  Elevator shall be installed by the manufacturer or by a manufacturer recommended installer with a minimum 5 years experience in the installation and service of traction elevators.

C. Inspection and Testing:  In accordance with requirements of local jurisdiction, obtain required permits, inspections and tests.

D. Prior to beginning work of this Section, attend a pre-installation meeting.  Owner, Design Professional, and contractors with adjacent or related work shall attend.

1.07 DELIVERY, STORAGE AND HANDLING

A.
Coordinate delivery of elevator material throughout construction.

B.
Store elevator materials in protected environment in accordance with manufacturer recommendations.

1.08 WARRANTY

A.
Provide Manufacturer warranty for a period of one year.  Warranty period to begin upon elevator final acceptance.  Warranty covers defects in materials and workmanship. Damage due to ordinary use, vandalism, improper or insufficient maintenance, misuse, or neglect do not constitute defective material or workmanship. 

1.09 MAINTENANCE SERVICE

A. Provide maintenance service consisting of examinations and adjustments of the elevator equipment for a period of 12 months after date of elevator final acceptance.

B. Maintenance service shall be provided by elevator manufacturers’ service personnel. Manufacturer recommended parts and supplies shall be used in maintenance service as in the original manufacture and installation.

C. Maintenance service be performed during regular working hours of regular working days and shall include regular time call back service.  

D. Maintenance service shall not include adjustments, repairs or replacement of parts due to negligence, misuse, abuse or accidents.

PART 2 - PRODUCTS
2.01 MANUFACTURER

A. Provide machine room-less EcoSpace™ traction elevators by KONE, Inc. (www.kone.com) consisting of the following components:

1. 
AC gearless machine using embedded permanent magnets mounted to the guide rails.

2.
Non-proprietary controls and technology.

2.02 MATERIALS

A. Steel

1. Sheet Steel for Exposed Work: Stretcher-leveled, cold-rolled, commercial-quality carbon steel, complying with ASTM A366, matte finish.

2. Sheet Steel for Unexposed Work: Hot-rolled, commercial-quality carbon steel, pickled and oiled, complying with ASTM A569.

3. Structural Steel Shapes and Plates: ASTM A36 and AISI 1018.

B. Stainless Steel: Type 300 Series complying with ASTM A167, with standard tempers and hardness required for fabrication, strength and durability.

1. Supply with mechanical finish on fabricated work in the location shown or specified with texture and reflectivity required (Federal and NAAMM nomenclature). Protect with adhesive plastic film or paper covering.

2. All finishes specified as “satin” to be manufacturer’s standard directional polish that complies with commercial No. 4 requirements.

3. Material may vary per specification.

C. Aluminum: Extrusions per ASTM B221; sheet and plate per ASTM B209.

D. Plastic Laminate: ASTM E84 Class B and NEMA LD3, 0-1/20” (1.3 mm) up to 0-1/16” (1.6 mm) nominal thickness.  Exposed surfaces to have color selected by architect from manufacturer’s standard selection.

E. Fire-Retardant Treated Particleboard Panels: Minimum 0-1/2” (13 mm) thick backup for plastic laminate veneered panels, provided with suitable anti-warp backing; to meet ASTM E84 Class “A” rating with flame-spread rating of 25 or less.

F. Paint:

1. Concealed Steel and Iron: Clean metal of oil, grease, scale and other foreign matter and paint one shop coat of manufacturer’s standard rust-resistant primer. Galvanized metal need not be painted.

2. Exposed Steel: Clean exposed metal of oil, grease, scale and other foreign matter. Eliminate any dents, scratches, or other defects that would affect the final finish. For material delivered with primer coat only, apply enamel primer. For material delivered with a finish coat, apply two coats enamel.
2.03 EQUIPMENT: CONTROL COMPONENTS

A. Controller:  Provide microcomputer based control system to perform all of the functions.  The system shall also perform car and group operational control. 

1. All high voltage (110V or above) contact points inside the controller cabinet shall be protected from accidental contact in a situation where the controller doors are open.

2. Controller shall be separated into two distinct halves; Motor Drive side and Control side. High voltage motor power conductors shall be routed and physically segregated from the rest of the controller.

3. Provide a serial cardrack and main CPU board containing a non-erasable EPROM and operating system firmware.

4. Variable field parameters and adjustments shall be contained in a non-volatile memory module. 

B. Drive: Provide Variable Voltage Variable Frequency AC drive system to develop high starting torque with low starting current.

C. Controller Location:  Locate controller adjacent to the hoistway at the top landing in an {integral control space or adjacent control space}. 

2.04 EQUIPMENT: HOISTWAY COMPONENTS

A. Machine:  AC gearless machine, with permanent magnet synchronous motor, direct current electro-mechanical disc brakes and integral traction drive sheave, mounted to the car guide rail at the top of the hoistway.

B. Governor:  Friction type over-speed governor rated for the duty of the elevator specified.

C. Buffers, Car and Counterweight:  Polyurethane buffer.

D. Hoistway Operating Devices:

1. Emergency stop switch in the pit

2. Terminal stopping switches.

3. Emergency stop switch on the machine

E. Positioning System: System consisting of magnets and proximity switches.

F. Guide Rails and Attachments: Steel rails with brackets and fasteners. Side counterweight arrangements to have a dual-purposed bracket that combines one car rail with one counterweight rail on the machine side. Additional bracket supports the other counterweight rail on the machine side and a separate bracket supports the other car rail opposite the machine.

G. Ropes:  Provide five hoist ropes 10-mm diameter fabricated from steel wire wound about a steel core.
H. Governor Rope: Provide 3/8-inch diameter steel cable governor rope minimum eight strands wound about a sisal core center.

I. Fascia: Galvanized sheet steel shall be provided at the front of the hoistway.
J. Hoistway Entrances

1. Frames: 16-gauge sheet steel, bolted construction.

2. Sills: extruded aluminum.
3. Doors:  Hollow metal construction with vertical internal channel reinforcements.  

4. Fire Rating: Entrance and doors shall be UL fire-rated for 1-1/2 hour.

5. Entrance Finish:  #4 brushed stainless steel.
6. Entrance Markings Jamb Plates:  Provide standard entrance jamb tactile markings on both jambs, at all floors. Plates shall be surface mounted. Plate finish to be #4 brushed stainless steel. 
2.05 EQUIPMENT: CAR COMPONENTS

A. Car Frame: Provide car frame with adequate bracing to support the platform and car enclosure.

B. Platform: Platform shall be all steel construction. 

C. Car Guides: Provide guide-shoes mounted to top and bottom of both car and counterweight frame. Each guide-shoe assembly shall be arranged to maintain constant contact on the rail surfaces. Provide retainers in areas with Seismic design requirements.

D. Load weighing device shall be strain gauge type mounted to dead-end hitch attached atop the hoistway guide-rail.

E. Steel Cab 

1. Panels: Non-removable vertical panels, plastic laminate selected from standard manufacturer’s catalog of choices. Trim and base plate to be aluminum with brushed finish.

2. Car Front Finish: Brushed stainless steel.

3. Car Door Finish: Brushed stainless steel.

4. Ceiling: Ceiling: 

a. Aurora -LF73 Ceiling - suspended ceiling shall consist of white translucent polycarbonate panels set in frame of extruded natural satin finish with fluorescent lighting fixtures.

OR
b. Eclipsis [LF2 Ceiling] suspended ceiling shall consist of round diffusers set in stainless steel frame with fluorescent lighting fixtures. 

OR
c. Alba Chromatica [LF3 Ceiling] suspended ceiling shall consist of parallel rows of diffusers set in stainless steel frame with fluorescent lighting fixtures.

5. Handrail

a. {Flat Solid Metal} handrail of 3/8-inch thick by 2 inches tall.  Material to be {brushed stainless steel / matte aluminum}.  Rails to be located on sides of car enclosure.

OR
b. {Round Tubular Metal} of 3/8-inch by 1½ inch outside diameter.  Material to be {brushed stainless steel / matte aluminum}.  Rails to be located on sides of car enclosure. Provide flat end-caps of same finish and material as the handrail.

(Specifier Note: Total thickness of flooring, including substrate, shall not exceed 0-1/2” in depth, and finished flooring weight may not exceed 3 lbs./ft2.)
6. Flooring: By others.

7. Threshold:  Extruded aluminum.

F. Emergency Car Signals

1. Emergency Siren: Siren mounted on top of cab that is activated when the alarm button in the car operating panel is engaged.  Siren shall have rated sound pressure level of 80 dB(A) at a distance of three feet from device.  Siren shall respond with a delay of not more than one second after activation of alarm button.

2. Emergency Car Lighting: Provide emergency power unit employing a 12-volt sealed rechargeable battery and totally static circuits shall illuminate the elevator car and provide current to the alarm bell in the event of building power failure. 

3. Emergency Exit Contact: An electrical contact shall be provided on the car-top exit.

G. Ventilation: {Natural ventilation at the top and bottom of side and rear walls} OR {Power ventilation two-speed fan}.

2.06 EQUIPMENT: SIGNAL DEVICES AND FIXTURES

A. Car Operating Panel: Provide car operating panel with all push buttons, key switches, and message indicators for elevator operation.

1. KSS 370 Fixtures:  Provide integral car operating panel.  Panel shall contain a bank of round, mechanical, illuminated buttons marked to correspond to landings served, emergency call button, door open button, door close button, and key switches for lights, inspection, and exhaust fan.  Buttons have amber illumination (halo). All buttons to have raised text and Braille marking on left hand side.  The car operating display panel shall be amber DOT-matrix. All texts, when illuminated, shall be amber. The car operating panel shall have a brushed stainless steel finish.

2. Additional features of car operating panel shall include:

a. Car Position Indicator within operating panel (amber). 

b. Elevator Data Plate marked with elevator capacity and car number on car top.

c. Illuminated alarm button with raised markings.
d. In car stop key switch.

e. Firefighter’s hat.

f. Firefighter’s Phase II Key-switch.

g. Call Cancel Button.

h. Help Button/Communicator.  Activation of help button will initiate two-way communication between car and a location inside the building, switching over to alternate location if call is unanswered, where personnel are available to take the appropriate action.  Visual indicators are provided for call initiation and call acknowledgement.

i. Firefighter’s Phase II emergency in-car operating instructions. 

j. Landing Passing Signal: A chime bell shall sound in the car to signal that the car is either stopping at or passing a floor served by the elevator.

B. Hall Fixtures: Hall fixtures shall be provided with necessary push buttons and key switches for elevator operation.  Hall fixtures shall have a brushed stainless steel finish.

1. KSS 370 Fixtures: Hall fixtures shall feature round, mechanical, buttons in applied mount face frame. Hall fixtures shall correspond to options available from that landing. Buttons shall be {flat flush / ¼ inch projecting} in vertically mounted fixture. Hall lanterns and hall indicators shall be illuminated by means of amber illumination. 

C. Car Lantern and Chime: A directional lantern visible from the corridor shall be provided in the car entrance.  When the car stops and the doors are opening, the lantern shall indicate the direction in which the car is to travel and a chime will sound. The chime will sound once for up and twice for down.

D. Hall call cutout key-switches to disable activation of hall buttons, locate at {XX landing}.
2.07 EQUIPMENT: ELEVATOR OPERATION AND CONTROLLER

A. Elevator Operation

1. Simplex Collective Operation: Using a microprocessor-based controller, operation shall be automatic by means of the car and hall buttons. If all calls in the system have been answered, the car shall park at the last landing served.
B. Standard Operating Features to include:

1. Full Collective Operation 

2. Fan and Light Control.

3. Load Weighing Bypass.

4. Independent Service.

5. Ascending Car Uncontrolled Movement Protection

6. Firefighters' Service Phase I and Phase II.

7. Top of Car Inspection Station.

C. Additional Operating Features to include:

(Specifier Note:  The following features are optional.  DELETE features not required for project.)
1. Independent Service.

2. Zoned Access at Bottom Landing.

3. Zoned Access at Upper Landing.

4. Car Secure Access.

5. Provision for Card Reader in Car (Card Reader provided and Installed by others).

6. Card-reader provisions in the hallway.

7. Automatic Standby Power Operation with Manual Override.

(Specifier Note:  Following is an explanation of the Automatic Standby Power Operation with Manual Override feature and provided for information.  You may elect to include or DELETE.

This operation shall return each car automatically to a designated landing when the system is initially switched to standby power.  
D. Elevator Control System for Inspections and Emergency

1. Provide devices within controller to run the elevator in inspection operation.

2. Provide devices on car top to run the elevator in inspection operation

3. Provide within controller an emergency stop switch to disconnect power from the brake and prevents motor from running.

4. Provide the means from the controller to mechanically lift and control the elevator brake to safely bring car to nearest available landing when power is interrupted.

5. Provide the means from the controller to reset the governor over speed switch and also trip the governor.

6. Provide the means from the controller to reset the emergency brake when set because of an unintended car movement or ascending car over speed.

2.08 EQUIPMENT:  DOOR OPERATOR AND CONTROL

A. Door Operator: A closed loop permanent magnet VVVF high-performance door operator shall be provided to open and close the car and hoistway doors simultaneously. Door movement shall be cushioned at both limits of travel. Electro-mechanical interlock shall be provided at each hoistway entrance to prevent operation of the elevator unless all doors are closed and locked. An electric contact shall be provided on the car at each car entrance to prevent the operation of the elevator unless the car door is closed. 

B. The door operator shall be arranged so that, in case of interruption or failure of electric power, the doors can be readily opened by hand from within the car, in accordance with applicable code. Emergency devices and keys for opening doors from the landing shall be provided as required by local code.

C. Doors shall open automatically when the car has arrived at or is leveling at the respective landings. Doors shall close after a predetermined time interval or immediately upon pressing of a car button. A door open button shall be provided in the car. Momentary pressing of this button shall reopen the doors and reset the time interval.

D. Door hangers and tracks shall be provided for each car and hoistway door. Tracks shall be contoured to match the hanger sheaves. The hangers shall be designed for power operation with provisions for vertical and lateral adjustment. Hanger sheaves shall have polyurethane tires and pre-lubricated sealed-for-life bearings.

E. Electronic Door Safety Device.  The elevator car shall be equipped with an electronic protective device extending the full height of the car. When activated, this sensor shall prevent the doors from closing or cause them to stop and reopen if they are in the process of closing. The doors shall remain open as long as the flow of traffic continues and shall close shortly after the last person passes through the door opening.

PART 3 – EXECUTION

3.1 EXAMINATION 

A. Field measure and examine substrates, supports, and other conditions under which elevator work is to be performed.

B. Do not proceed with work until unsatisfactory conditions are corrected

3.2 PREPARATION 

A. Coordinate installation of anchors, bearing plates, brackets and other related accessories

3.3 INSTALLATION  

A. Install equipment, guides, controls, car and accessories in accordance with manufacturer installation methods and recommended practices.

B. Properly locate guide rails and related supports at locations in accordance with manufacturer’s recommendations and approved shop drawings. Anchor to building structure using isolation system to minimize transmission of vibration to structure.

C. All hoistway frames shall be securely fastened to fixing angles mounted in the hoistway.  Coordinate installation of sills and frames with other trades. 

D. Lubricate operating system components in accordance with manufacturer recommendations.

E. Perform final adjustments, and necessary service prior to substantial completion

3.4 TESTING AND INSPECTIONS

A. Perform recommended and required testing in accordance with authority having jurisdiction.

B. Obtain required permits and provide originals to Owner’s Representative.

3.5 DEMONSTRATION

A. Prior to substantial completion, instruct Owner’s Representative on the proper function and required daily maintenance of elevators. Instruct personnel on emergency procedures

3.6 SCHEDULE

(Specifier Note:  Provide elevator schedule information for each system configuration.  SELECT appropriate options and DELETE options not required.  Contact KONE Product Representative for assistance.) 
A. Elevator Equipment:  EcoSpace™ gearless traction elevator

B. Equipment Control:  Microprocessor KCM831 control system

C. Quantity & Elevator Numbers: One – Elevator #1

D. Number of Stops: (enter number of front and rear stops – maximum 7)
E. Openings: Front and Rear Openings
F. Rise: (enter rise in feet and inches – maximum 63’-0”)
G. Rated Capacity: {2000#} OR {2500#}.

H. Rated Speed: 150 fpm

I. Clear Inside Dimensions (W x D): (2000# - ADA wheelchair minimum) {5’-8” x 4’-3”}  OR (2500# NEII stretcher-accessible with side slide door) {6’-8” x 4’-3”}
J. Cab Height: {8’-0”} OR {9’-0”} OR {10’-0”}
K. Clear height under suspended ceiling: {(8’-0” cab height) 7’-7”} OR  {(9’-0” cab height) 8’-7”}  OR {(10’-0” cab height) 9’-7”}
L. Entrance Width & Type: (match to selected capacity, SELECT appropriate options and DELETE remaining options)
1. 2000# 3’-0”  {Single slide left} OR {Single slide right}
2. 2500# 3’-6” {Single slide left} OR {Single slide right} OR {Center opening}
M. Entrance Height: {7’-0”} OR {8’-0”} OR {9’-0”}
N. Main Power Supply: {208, 240} OR {480 Volts + 5%, three-phase}
O. Operation: Simplex Collective Operation
P. Machine Location:  Mounted on car guide rail

END OF SECTION 

KONE  Inc.

Page 1 of 1
EcoSpace Traction Elevator 

10/14/2004
Guide Specification – Long Form
14 21 00
KONE  Inc.

Page 9 of 9
EcoSpace Traction Elevator 

9/7/04

Guide Specification 
14 21 00

MKT-05-0023 Rev6

