COUNTRY GARDENS


SECTION 16073
HANGERS AND SUPPORTS FOR ELECTRICAL SYSTEMS
Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Hangers and supports for electrical equipment and systems.

2. Construction requirements for concrete bases.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. EMT:  Electrical metallic tubing.

B. IMC:  Intermediate metal conduit.

C. RMC:  Rigid metal conduit.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design supports for multiple raceways, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

B. Design supports for multiple raceways capable of supporting combined weight of supported systems and its contents.

C. Design equipment supports capable of supporting combined operating weight of supported equipment and connected systems and components.

Consult structural engineer on safety factor to be specified in paragraph below, or delete and let applicable code determine strength.  Retain below if strength that exceeds code requirements is desired.

D. Rated Strength:  Adequate in tension, shear, and pullout force to resist maximum loads calculated or imposed for this Project, with a minimum structural safety factor of five times the applied force.

1.5 SUBMITTALS

Retain this Article for large or complex projects.

A. Product Data:  For the following:

1. Steel slotted support systems.

2. Nonmetallic slotted support systems.

Retain paragraph and subparagraphs below if supporting systems are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify supporting system's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings: Show fabrication and installation details and include calculations for the following:

Adjust list below to suit Project.

1. Trapeze hangers.  Include Product Data for components.

2. Steel slotted channel systems.  Include Product Data for components.

3. Nonmetallic slotted channel systems.  Include Product Data for components.

4. Equipment supports.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance"Article.

C. Welding certificates.

1.6 QUALITY ASSURANCE

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

B. Comply with NFPA 70.

1.7 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  

PART 2 -  PRODUCTS

2.1 SUPPORT, ANCHORAGE, AND ATTACHMENT COMPONENTS

Retain this Article to specify default product requirements for basic supporting devices.  Items to be supported include raceways, cables, wireways, cable trays, busways, boxes, cabinets, equipment, and other electrical products.  Where support materials or workmanship is unique to a particular product, specify unique features that are the exception to these default requirements in the Section that specifies the product.  Coordinate specifications for supporting devices with structural engineer and with Drawings.

A. Steel Slotted Support Systems:  Comply with MFMA-4, factory-fabricated components for field assembly.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

a. Allied Tube & Conduit.

b. Cooper B-Line, Inc.; a division of Cooper Industries.

c. ERICO International Corporation.

d. GS Metals Corp.

e. Thomas & Betts Corporation.

f. Unistrut; Tyco International, Ltd.

g. Wesanco, Inc.

Retain one or more coating systems in first three subparagraphs below.  If retaining more than one, specify in Part 3 where each coating system is required.

2. Metallic Coatings:  Hot-dip galvanized after fabrication and applied according to MFMA-4.

3. Nonmetallic Coatings:  Manufacturer's standard PVC, polyurethane, or polyester coating applied according to MFMA-4.

4. Painted Coatings:  Manufacturer's standard painted coating applied according to MFMA-4.

5. Channel Dimensions:  Selected for applicable load criteria.

If retaining first paragraph and subparagraphs below, coordinate with Part 3 and with Drawings to indicate where nonmetallic channel is to be used.

B. Nonmetallic Slotted Support Systems:  Structural-grade, factory-formed, glass-fiber-resin channels and angles with 9/16-inch diameter holes at a maximum of 8 inches o.c., in at least 1 surface.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

a. Allied Tube & Conduit.

b. Cooper B-Line, Inc.; a division of Cooper Industries.

c. Fabco Plastics Wholesale Limited.

d. Seasafe, Inc.

2. Fittings and Accessories:  Products of channel and angle manufacturer and designed for use with those items.

3. Fitting and Accessory Materials:  Same as channels and angles.

4. Rated Strength:  Selected to suit applicable load criteria.

C. Raceway and Cable Supports:  As described in NECA 1 and NECA 101.

D. Conduit and Cable Support Devices:  Steel or Steel and malleable-iron hangers, clamps, and associated fittings, designed for types and sizes of raceway or cable to be supported.

E. Support for Conductors in Vertical Conduit:  Factory-fabricated assembly consisting of threaded body and insulating wedging plug or plugs for non-armored electrical conductors or cables in riser conduits.  Plugs shall have number, size, and shape of conductor gripping pieces as required to suit individual conductors or cables supported.  Body shall be malleable iron.

F. Structural Steel for Fabricated Supports and Restraints:  ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

Coordinate paragraph and subparagraphs below with installation requirements in Part 3.

G. Mounting, Anchoring, and Attachment Components:  Items for fastening electrical items or their supports to building surfaces include the following:

Verify suitability of fasteners in subparagraph below for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

1. Powder-Actuated Fasteners:  Threaded-steel stud, for use in hardened portland cement concrete, steel, or wood, with tension, shear, and pullout capacities appropriate for supported loads and building materials where used.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

a. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1) Hilti Inc.

2) ITW Ramset/Red Head; a division of Illinois Tool Works, Inc.

3) MKT Fastening, LLC.

4) Simpson Strong-Tie Co., Inc.; Masterset Fastening Systems Unit.

2. Mechanical-Expansion Anchors:  Insert-wedge-type, zinc-coated steel, for use in hardened portland cement concrete with tension, shear, and pullout capacities appropriate for supported loads and building materials in which used.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

a. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1) Cooper B-Line, Inc.; a division of Cooper Industries.

2) Empire Tool and Manufacturing Co., Inc.

3) Hilti Inc.

4) ITW Ramset/Red Head; a division of Illinois Tool Works, Inc.

5) MKT Fastening, LLC.

3. Concrete Inserts:  Steel or malleable-iron, slotted support system units similar to MSS Type 18; complying with MFMA-4 or MSS SP-58.

4. Clamps for Attachment to Steel Structural Elements:  MSS SP-58, type suitable for attached structural element.

5. Through Bolts:  Structural type, hex head, and high strength.  Comply with ASTM A 325.

6. Toggle Bolts:  All-steel springhead type.

7. Hanger Rods:  Threaded steel.

2.2 FABRICATED METAL EQUIPMENT SUPPORT ASSEMBLIES

Equipment supports in this Article require calculation of load and strength for each component and detailing of each assembly.  Coordinate specifications for each equipment support with structural engineer and with Drawings.

A. Description:  Welded or bolted, structural-steel shapes, shop or field fabricated to fit dimensions of supported equipment.

PART 3 -  EXECUTION

3.1 APPLICATION

A. Comply with NECA 1 and NECA 101 for application of hangers and supports for electrical equipment and systems except if requirements in this Section are stricter.

In first paragraph below, support spacings in NECA 1, Table 1, are more detailed and specific and generally stricter than those permitted by NFPA 70 for EMT, IMC, and RMC.  Revise to suit Project, and consider retaining reference to NECA table for critical projects.

B. Maximum Support Spacing and Minimum Hanger Rod Size for Raceway:  Space supports for EMT, IMC, and RMC as required by NFPA 70.  Minimum rod size shall be 1/4 inch in diameter.

C. Multiple Raceways or Cables:  Install trapeze-type supports fabricated with steel slotted or other support system, sized so capacity can be increased by at least 25 percent in future without exceeding specified design load limits.

1. Secure raceways and cables to these supports with two-bolt conduit clamps.

Retain paragraph below for projects where seismic design requirements do not apply.  Consider retaining for light-commercial projects only.

D. Spring-steel clamps designed for supporting single conduits without bolts may be used for 1-1/2-inch and smaller raceways serving branch circuits and communication systems above suspended ceilings and for fastening raceways to trapeze supports.

3.2 SUPPORT INSTALLATION

Consult structural engineer for requirements in this Article.

A. Comply with NECA 1 and NECA 101 for installation requirements except as specified in this Article.

Retain first paragraph below to permit raceways running perpendicular to bar joists and trusses to be supported by letting them rest within the joist or truss openings.  NECA 1 does not mention this method.  If seismic design requirements apply, consult structural engineer or authorities having jurisdiction before permitting this support method and specify seismic requirements in Division 16 Section "Vibration and Seismic Controls for Electrical Systems."

B. Raceway Support Methods:  In addition to methods described in NECA 1, EMT, IMC, and RMC may be supported by openings through structure members, as permitted in NFPA 70.

C. Strength of Support Assemblies:  Where not indicated, select sizes of components so strength will be adequate to carry present and future static loads within specified loading limits.  Minimum static design load used for strength determination shall be weight of supported components plus 200 lb.

D. Mounting and Anchorage of Surface-Mounted Equipment and Components:  Anchor and fasten electrical items and their supports to building structural elements by the following methods unless otherwise indicated by code:

1. To Wood:  Fasten with lag screws or through bolts.

2. To New Concrete:  Bolt to concrete inserts.

3. To Masonry:  Approved toggle-type bolts on hollow masonry units and expansion anchor fasteners on solid masonry units.

4. To Existing Concrete:  Expansion anchor fasteners.

Retain first subparagraph below if powder-actuated devices are allowed.  Consider deleting if Project contains both lightweight and standard-weight concrete or more than one thickness of concrete slab.

5. Instead of expansion anchors, powder-actuated driven threaded studs provided with lock washers and nuts may be used in existing standard-weight concrete 4 inches thick or greater.  Do not use for anchorage to lightweight-aggregate concrete or for slabs less than 4 inches thick.

6. To Steel:  Welded threaded studs complying with AWS D1.1/D1.1M, with lock washers and nuts or Beam clamps (MSS Type 19, 21, 23, 25, or 27) complying with MSS SP-69.

7. To Light Steel:  Sheet metal screws.

8. Items Mounted on Hollow Walls and Nonstructural Building Surfaces:  Mount cabinets, panelboards, disconnect switches, control enclosures, pull and junction boxes, transformers, and other devices on slotted-channel racks attached to substrate by means that meet seismic-restraint strength and anchorage requirements.

E. Drill holes for expansion anchors in concrete at locations and to depths that avoid reinforcing bars.

3.3 INSTALLATION OF FABRICATED METAL SUPPORTS

Coordinate installation requirements in this Article with structural engineer.

A. Cut, fit, and place miscellaneous metal supports accurately in location, alignment, and elevation to support and anchor electrical materials and equipment.

B. Field Welding:  Comply with AWS D1.1/D1.1M.

3.4 CONCRETE BASES

Coordinate this Article with Division 3 Section "Cast-in-Place Concrete" or "Cast-in-Place Concrete (Limited Applications)."

Coordinate paragraphs and subparagraphs below with Sections specifying supported equipment.

A. Construct concrete bases of dimensions indicated but not less than 4 inches larger in both directions than supported unit, and so anchors will be a minimum of 10 bolt diameters from edge of the base.

B. Use 3000-psi minimum, 28-day compressive-strength concrete.  

C. Anchor equipment to concrete base.

1. Place and secure anchorage devices.  Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

2. Install anchor bolts to elevations required for proper attachment to supported equipment.

3. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

3.5 PAINTING

Retain paragraph and subparagraph below if a Division 9 painting Section is not in Project Manual.

A. Touchup:  Clean field welds and abraded areas of shop paint.  Paint exposed areas immediately after erecting hangers and supports.  Use same materials as used for shop painting.  Comply with SSPC-PA 1 requirements for touching up field-painted surfaces.

1. Apply paint by brush or spray to provide minimum dry film thickness of 2.0 mils.

Retain first paragraph below if a Division 9 painting Section is in Project Manual.

B. Touchup:  Comply with requirements in Division 9 painting Sections for cleaning and touchup painting of field welds, bolted connections, and abraded areas of shop paint on miscellaneous metal.

C. Galvanized Surfaces:  Clean welds, bolted connections, and abraded areas and apply galvanizing-repair paint to comply with ASTM A 780.

END OF DOCUMENT
HANGERS AND SUPPORTS FOR ELECTRICAL SYSTEMS
16073 - 6

