COUNTRY GARDENS


SECTION 16120
CONDUCTORS AND CABLES
Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Copyright 2002, The American Institute of Architects (AIA)

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Building wires and cables rated 600 V and less.

2. Connectors, splices, and terminations rated 600 V and less.

3. Sleeves and sleeve seals for cables.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. EPDM:  Ethylene-propylene-diene terpolymer rubber.

B. NBR:  Acrylonitrile-butadiene rubber.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

B. Qualification Data:  For testing agency.

Retain paragraph below if Contractor is responsible for field quality-control testing.

C. Field quality-control test reports.

1.5 QUALITY ASSURANCE

Retain first paragraph and subparagraph below if Contractor is required to provide services of an independent testing agency in Part 3 "Field Quality Control" Article.  Qualification requirements supplement those specified in Division 1 Section "Quality Requirements," which also includes the definition for NRTL (nationally recognized testing laboratory).

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

1.6 COORDINATION

A. Set sleeves in cast-in-place concrete, masonry walls, and other structural components as they are constructed.

PART 2 -  PRODUCTS

2.1 CONDUCTORS AND CABLES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Alcan Products Corporation; Alcan Cable Division.

2. American Insulated Wire Corp.; a Leviton Company.

3. General Cable Corporation.

4. Senator Wire & Cable Company.

5. Southwire Company.

B. Copper Conductors:  Comply with NEMA WC 70.

C. Conductor Insulation:  Comply with NEMA WC 70 for Types THHN-THWN
2.2 CONNECTORS AND SPLICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. AFC Cable Systems, Inc.

2. Hubbell Power Systems, Inc.

3. O-Z/Gedney; EGS Electrical Group LLC.

4. 3M; Electrical Products Division.

5. Tyco Electronics Corp.

B. Description:  Factory-fabricated connectors and splices of size, ampacity rating, material, type, and class for application and service indicated.

2.3 SLEEVES FOR CABLES

A. Steel Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.

Consider retaining first paragraph below if cables penetrate exterior walls below grade.

B. Cast-Iron Pipe Sleeves:  Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.

C. Sleeves for Rectangular Openings:  Galvanized sheet steel with minimum 0.052- or 0.138-inch  thickness as indicated and of length to suit application.

D. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 7 Section "Through-Penetration Firestop Systems."

2.4 SLEEVE SEALS

Retain this Article if annular space between pipe sleeves and cables must be sealed against hydrostatic pressure.  Sleeve seals are usually furnished with EPDM sealing elements, plastic pressure plates, and carbon-steel bolts.  NBR and silicone sealing elements, carbon- and stainless-steel pressure plates, and stainless-steel bolts are available for special applications.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Advance Products & Systems, Inc.

2. Calpico, Inc.

3. Metraflex Co.

4. Pipeline Seal and Insulator, Inc.

B. Description:  Modular sealing device, designed for field assembly, to fill annular space between sleeve and cable.

1. Sealing Elements:  EPDM  interlocking links shaped to fit surface of cable or conduit.  Include type and number required for material and size of raceway or cable.

PART 3 -  EXECUTION

3.1 CONDUCTOR MATERIAL APPLICATIONS

A. Feeders:  Copper.  Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

B. Branch Circuits:  Copper.  Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

3.2 CONDUCTOR INSULATION AND MULTICONDUCTOR CABLE APPLICATIONS AND WIRING METHODS

This Article provides examples of application requirements for conductors and cables.  Edit to select wiring methods for various environments in Project.  Add other methods if required.  Revise conductor insulation and cable type designations to suit Project conditions, authorities having jurisdiction, and practice.  Refer to NFPA 70 and to UL's "Electrical Construction Equipment Directory" for additional application information about conductor sizes, insulation temperature ratings in cables, and product-use classifications and restrictions.

See Editing Instruction No. 2 in the Evaluations for use of Type MI cable as service entrance conductor inside a building.

A. Service Entrance:  Type THHN-THWN, single conductors in raceway.

B. Exposed Feeders:  Type THHN-THWN, single conductors in raceway.

C. Feeders Concealed in Ceilings, Walls, Partitions, and Crawlspaces:  Type THHN-THWN, single conductors in raceway.

Coordinate first paragraph below with Division 2 Section "Underground Ducts and Utility Structures."

D. Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type THHN-THWN, single conductors in raceway.

E. Exposed Branch Circuits, Including in Crawlspaces:  Type THHN-THWN, single conductors in raceway.

F. Branch Circuits Concealed in Ceilings, Walls, and Partitions:  Type THHN-THWN, single conductors in raceway.

Coordinate first paragraph below with Division 2 Section "Underground Ducts and Utility Structures."

G. Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type THHN-THWN, single conductors in raceway.

H. Cord Drops and Portable Appliance Connections:  Type SO, hard service cord with stainless-steel, wire-mesh, strain relief device at terminations to suit application.

I. Class 1 Control Circuits:  Type THHN-THWN, in raceway.

J. Class 2 Control Circuits:  Type THHN-THWN, in raceway.

3.3 INSTALLATION OF CONDUCTORS AND CABLES

A. Conceal cables in finished walls, ceilings, and floors, unless otherwise indicated.

B. Use manufacturer-approved pulling compound or lubricant where necessary; compound used must not deteriorate conductor or insulation.  Do not exceed manufacturer's recommended maximum pulling tensions and sidewall pressure values.

C. Use pulling means, including fish tape, cable, rope, and basket-weave wire/cable grips, that will not damage cables or raceway.

D. Install exposed cables parallel and perpendicular to surfaces of exposed structural members, and follow surface contours where possible.

3.4 CONNECTIONS

A. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

B. Make splices and taps that are compatible with conductor material and that possess equivalent or better mechanical strength and insulation ratings than unspliced conductors.

Delete subparagraph below unless aluminum conductors are specified.

C. Wiring at Outlets:  Install conductor at each outlet, with at least 6 inches  of slack.

3.5 SLEEVE INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Concrete Slabs and Walls:  Install sleeves for penetrations unless core-drilled holes or formed openings are used.  Install sleeves during erection of slabs and walls.

B. Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.

C. Rectangular Sleeve Minimum Metal Thickness:

1. For sleeve rectangle perimeter less than 50 inches and no side greater than 16 inches  , thickness shall be 0.052 inch.

2. For sleeve rectangle perimeter equal to, or greater than, 50 inches and 1 or more sides equal to, or greater than, 16 inches, thickness shall be 0.138 inch.

D. Fire-Rated Assemblies:  Install sleeves for penetrations of fire-rated floor and wall assemblies unless openings compatible with firestop system used are fabricated during construction of floor or wall.

Edit first paragraph below as required for 2-inch (50-mm) extension above floor.

E. Cut sleeves to length for mounting flush with both wall surfaces.

F. Extend sleeves installed in floors 2 inches above finished floor level.

Edit paragraph below as required for Project design conditions and seismic-criteria status.

G. Size pipe sleeves to provide 1/4-inch annular clear space between sleeve and cable unless sleeve seal is to be installed or unless seismic criteria require different clearance.

Retain first paragraph below if external sealing is required.

H. Seal space outside of sleeves with grout for penetrations of concrete and masonry.

I. Interior Penetrations of Non-Fire-Rated Walls and Floors:  Seal annular space between sleeve and cable, using joint sealant appropriate for size, depth, and location of joint.
J. Fire-Rated-Assembly Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at cable penetrations.  Install sleeves and seal with firestop materials.
K. Roof-Penetration Sleeves:  Seal penetration of individual cables with flexible boot-type flashing units applied in coordination with roofing work.

L. Aboveground Exterior-Wall Penetrations:  Seal penetrations using sleeves and mechanical sleeve seals.  Size sleeves to allow for 1-inch annular clear space between pipe and sleeve for installing mechanical sleeve seals.

3.6 SLEEVE-SEAL INSTALLATION

A. Install to seal underground exterior-wall penetrations.

B. Use type and number of sealing elements recommended by manufacturer for cable material and size.  Position cable in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between cable and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

3.7 FIRESTOPPING

A. Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly. 

3.8 FIELD QUALITY CONTROL

Retain one of two paragraphs below that identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain requirement for field quality-control test reports in "Submittals" Article.

Retain paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections and prepare test reports.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by either of the entities in two paragraphs above.

B. Tests and Inspections:

Performing NETA tests on all conductors and cables can be expensive.  Consider limiting testing to a certain group of conductors, such as service entrance and feeder conductors, or to those conductors feeding critical equipment and services.  To require all conductors and cables to be tested, delete option in first subparagraph below and delete associated subparagraph.

1. After installing conductors and cables and before electrical circuitry has been energized, test service entrance and feeder conductors for compliance with requirements.

2. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

Consider the cost and benefit of infrared scanning of cable and conductor splices before retaining subparagraph and associated subparagraphs below.

C. Test Reports:  Prepare a written report to record the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

D. Remove and replace malfunctioning units and retest as specified above.

END OF DOCUMENT
CONDUCTORS AND CABLES

16120 - 6

