DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

 June 26, 2008
St. Tammany Parish, Facilities Management

P. O. Box 628

Covington, LA 70434

Attn: Bruce Crouch

Ref:
St. Tammany Parish Administration Complex


520 Old Spanish Trail


Slidell, LA 70458

Dear Mr. Crouch

In response to your letter dated June 13, 2008, I have prepared this letter and overlay drawings for your review and comment.

1st Floor-E-1PVAV Heaters moved slightly and Thermostats retained their original position.  VAV 1-4 is



shown on Drawing E-2P, at AHU-1 on the Mezzanine.

2nd Floor-E-2PVAV 2-1 moved from the corridor to room 209.



VAV 2-2 and Thermostat moved from Room 216 to Room 215.



VAV 2-3 and Thermostat moved from Room 219 to Room 216.



VAV 2-4 and Thermostat moved from Room 208 to Room 219.



VAV 2-5 moved south in Room 208 to the original position of VAV 2-4.

VAV 2-6 Duct Heater and Thermostat moved from Room 211 to the middle of Room 208.

VAV 2-7 was a Duct Heater only in the Ladies Restroom, Room 206 and was moved to Room 208, and a VAV unit was added.

VAV 2-8, located in Room 214 is new.

VAV 2-9 is new and replaced VAV 2-7 Duct Heater in the Ladies Restroom, Room 206 and a VAV unit was added.

VAV 2-10 is new and replaced VAV Duct Heater 2-6 in Room 211.

VAV 2-11, located in Room 209 is new.


3rd Floor-E-3PVAV 3-1, located in Room 304, remained in its original location.




VAV 3-2 and Thermostat moved from Room 324 to Room 319.




VAV 3-3 and Thermostat moved from Room 325 to Room 324.




VAV 3-4 and Thermostat moved from Room 322 to Room 325.




VAV 3-5 and Thermostat moved from the East Corridor to Room 326.




VAV 3-6 and Thermostat moved from Room 313 to Room 322.




VAV 3-7 and Thermostat moved from Room 315 to Room 323.

VAV 3-8 was a Duct Heater only in the Ladies Restroom, Room 307 and was moved to the East Corridor.

VAV 3-9, located in the East Corridor, is new.

VAV 3-10, and Thermostat moved from West Corridor to Room 313.

VAV 3-11, located in Ladies Restroom, Room 307, is new and replaced Duct Heater and a VAV unit was added.

VAV 3-12, located in Room 309, is new.


4th Floor-E-4PVAV 4-1 moved to the other side of Room 401.




VAV 4-2, located in Room 412, remained in its original location.




VAV 4-3, located in Room 414, remained in its original location.




VAV 4-4, located in Room 416, remained in its original location.




VAV 4-5, located in Room 417, remained in its original location.




VAV 4-6, located in Room 406, moved to the original location of VAV 4-7.




VAV 4-7 moved from Room 406 to room 407.




VAV 4-8, located in Room 409, moved to Room 410.

VAV 4-9, located in Room 404, Ladies Restroom, Room 404, moved to Room 405, and a VAV unit was added.

VAV 4-10, located in Room 404 Ladies Restroom, Room 404, replaced Duct Heater VAV 4-9, and a VAV unit was added.  It is also a new unit.

VAV 4-11, located in Room 402, is a new unit.

5th Floor-E-5PVAV 5-1 and Thermostat moved from Room 502 to Room 501.



VAV 5-2 and Thermostat moved from the West Corridor to Room 501.



VAV 5-3 and Thermostat moved from Room 501 to Room 508.



VAV 5-4 and Thermostat moved from Room 501 to Room 508.



VAV 5-5 and Thermostat, located in Room 511, remained in its original location.



VAV 5-6, located in Room 510, in the center, moved to the Southwest corner of Room 510.



VAV 5-7, located in Room 510, in the center, moved closer to the West wall of Room 510.



VAV 5-8, located in the East Corridor, moved to Room 510.

VAV 5-9, located in Lladies Restroom, room 504, moved to East Corridor, and a VAV unit was added.

VAV 5-10, located in Ladies Restroom, Room 504, is new and replaced Duct Heater VAV 5-9.

VAV 5-11, located in Room 502, is new.

6th Floor-E-6PVAV 6-1 and Thermostat, located in Room 611, moved to Room 601, same location as VAV 6-10 was.




VAV 6-2 and Thermostat,located in Room 611, East side, moved to Room 611, West side.

VAV 6-3 and Thermostat, located in Room 612, moved to Room 611, same location where VAV 6-1 was. 

VAV 6-4 and Thermostat, located in Room 613, moved to Room 611, same location as VAV 6-2 was.

VAV 6-5 and Thermostat, located in Room 613, moved to Room 612, same location as VAV 6-3 was.

VAV 6-6 and Thermostat, located in Room 606, moved to Room 613, same location as VAV 6-4 was.

VAV 6-7 and Thermostat, located in East Corridor, moved to Room 613, same location as VAV 6-5 was.




VAV 6-8 and Thermostat, located in Room 602, moved to Room 606




VAV 6-9 and Thermostat, located in Room 601, moved to Room 606.




VAV 6-10 and Thermostat, located in Room 601, moved to Room 610.

VAV 6-11 and Thermostat, located in Ladies Restroom, room 604, moved to East Corridor, and a VAV unit was added.

VAV 6-12, located in ladies restroom, room 604 is new and replaced duct heater VAV 6-11.

I reviewed the panel schedules and compared them to Star Mechanical’s latest submittal, dated 06-02-08.  Copies of the updated panel schedules will be sent to NATCO for distribution to the electrical contractor.  I created overlay drawings showing the old VAV locations versus the new locations.

The electrical drawings were not changed by 75%.  An actual figure is 9 of 15 drawings had changes on them, or actually 60% of the electrical drawings changed.  As you can see from the overlays,  a lot of things moved around, and when they did, the respective Circuit Callouts had to move with them.

I have reviewed Star Mechanical’s drawings and changed the Volt Amps for all affected VAV Units on the Panel Schedules.

Please feel free to contact me with any questions or concerns you may have.

Respectfully submitted,

Alan Brown 

