DAMMON ENGINEERING, INC.
dammonengineering.com
ARCHITECTS




ENGINEERS


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

7-19-2010

Bi- monthly meeting on 7-14-10

Items listed in courtesy review and are answered below

1) Approved fire marshal plans have been turned over to Landmark. (Bldg. plans/sprinkler/fire alarm.)
2) Wet copies of drawings and shop drawings, are here on file at Dammon Engineering for your viewing. If you need wet copies, Landmark shall resubmit for us to stamp.

3) Penetration details. Provided penetration details were provided at last meeting. Also see note 13 on sheet P-1 and the specifications for this project.

4) Mezz. Mechanical room design. State Fire Marshal has been contacted for clarification and is waiting to here from Linda Burch. I have verbal approval to build as per plan. Fire rated walls; ceiling and a/c shall have fire dampers. 

5) Resubmission of Fire Marshal plans. Have been resubmitted for clarification on certain items and not a package review. A full set is not needed for review; these have had a full review twice.

6) Knox Box is in route for all to sign. Please note this is not holding up job progress.

7) Fire Stair design; please see note #5.

8) Fire Stair Sprinkler heads. Please install Fire Sprinkler heads as approved by the State Fire Marshal and submittal.

9) Fire Pump Design; Please see note # 4

10) Chiller pipe collapsible collar, this item was submitted at last week’s meeting. 

11) A/C unit location; relocate to the south side of the stairs of the penthouse.

12) Penthouse house vent: no vent is needed as this space is conditioned.

13) Exit door stair design; this is for maintenance personnel only and not to the general public. No step is needed per the City and local Fire Marshal.

14) Hand rail spacing: Contractor shall make corrections to comply.

15) Handrail extensions; all handrail extensions shall conform to sheets H-1 and H-2.

16)  4x2 combo drain lines. This was a code issue and shall be addressed by the Contractor. 

17) Change out double T’s. This was a code issue and shall be addressed by the Contractor. 

18) Replace plastic Stub-outs.  This was a code issue and shall be addressed by the Contractor. 

19) Remove 45 degrees/p-traps, this was a code issue and shall be addressed by the Contractor. 

20) Install 4” Waste Lines.  

21) Replace plastic shut off valves. This is a code issue and shall be addressed by the Contractor. The change order was for the main lines only to change to PVC not the connections. 

22) PVC used in building. All PVC plumbing is approved for where it can be used per code.

23) Elevator shaft ventilation. This will require top and bottom vents for both elevators with only fire dampers located at the bottom per Dammon Engineering design.

24) Install drain line float shut off switch. This is a code issue and shall be addressed by the Contractor.

25) Ventilation Elevator Mechanical room. Install vent into existing pipe exterior pipe chase per Dammon Engineering design.

26) Ventilation for janitor’s closets. Not needed per existing code, build closest per plan.

27) Circulation space around HVAC units. This is an approved layout for an existing building. Build as per plan.

28) Smoke detectors to be provided. All smoke detectors shall be installed per code and plans.

29) Service entrance location. This is an approved location with all the proper disconnects.

30) Transformers in Air Return path. This is an existing condition space utilization. Build as per plans  

31) Duct clearance. ½” is the code and all clearances shall be maintained.

32) Install trapeze on lights. Install lights per manufacturer’s recommendations.

33) VAV switch locations. This is an approved layout for an existing building, build per plans.

34) Emergency lighting, this is an approved layout of emergency lighting, build per plans.

35) Exterior lighting at fire stair. Build as per lighting plan sheet E2L.

36) Shunt trip. There is no shunt trip required a disconnect is installed.

37) MDP location. This is an approved location and is installed.

Sincerely,

Dammon Engineering, Inc.
