March 12, 2009

Answers to electrical questions for TOWERS

1. Do we need a disconnect for the main power for the Fire Department, and if so, where?

The main breaker of MDP has a shunt trip that is controlled by a push button at the entrance to the building.

2. Please verify that main underground feeder to the building can be PVC; Tom says he discussed this with Mr. Pete.

PVC is OK.

3. Please verify that underground feeders should be 2-4,” or 3-3”, it is shown both ways on the drawings.

Underground conduits:

4-3” from MDP to pole

2-4” from 4th floor to pole

2-3” from 4th floor to pole
4. Please verify that main feeder cables should be 3-500 MCM for three phase service in lieu of 2-500 MCM shown.

A. Contractor furnishes and installs conduit.

B. Cleco furnishes circuit box and meter pan (contractor installs)

C. Cleco furnishes and installs conductors to building terminal (pull) box.

D. Contractor furnishes and installs terminal box and connector.

5. We need a decision on whether the transformer is pad or pole mounted.

Transformer pole mounted.

6. The plans don’t give anything clear I can find regarding a lighting layout for Conference Center 101.  What do we want to do there?

Somehow left off of latest drawing.  Natco was to save valance that existed, but chose to take it down.  It was on wall facing south, above wall that was renovated.

7. Please verify that the main service is 800 amp.

800 amp service.

