	PRIVATE 
DESIGN COORDINATION AND REVIEW - COMMENTSPRIVATE 

NAVAL SPECIAL WARFARE COMMAND, SAN DIEGO, CA
	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

Sam Martindale, P.E.
	CODE:

 N4412
	PHONE:

619-447-0772
	DATE:

12 Feb. 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY (SBT-22) NASA STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

65% Design

  

	NO.
	DWG.NO.

or

SPEC.SECT.
	COMMENTS
	A-E RESPONSE

	1
	All Dwgs
	Follow requirements in UFC 1-300-2 and UFC 1-300-09N. Use the standard labeling , section cut, and detail bubble labeling system. At the start of each discipline there should be a discipline title sheet with list of abbreviations and a legend of symbols use in the sheets with that discipline. 
	Corrected by designer.

	2
	Dwg T-1
	Index of Drawings: Add a column for NAVFAC Drawing Numbers. They are issued after the pre-final submittal via the NAVFACSE IPT PM. 
	Corrected by designer, column added to Sht. Cover 1.

	3
	Dwg T-2
	IBC 2006 Notes:  Please verify the references to sections 903 and 907. The wording is odd. You start out saying not required and then in the second sentence indicate the item will be provided. I believe the UFC governs each of these items and not the IBC. Please verify requirement list in the RFP and with the NAVFACSE Fire Protection Engineer.
	This is being re-written by the Architect to clarify compliance with each code involved.

	4
	Dwg S2.1
	This sheet is labeled as “Storage Building Foundation.”  This sheet shows the entire compound and the surrounding area and seems to be mislabeled. 

1.  A foundation plan needs to be a larger scale focusing on the buildings only, with a large enough scale to see all necessary dimensions and showing section cuts for details.

2. A foundation plan needs to show the coordinates for at least two corners to each building, otherwise how is an accurate location assured?  

3. Why show on these drawings the wash rack, the helo-pad, the new sheet pile wall, and the launch ramp work, when none of these options have been awarded? 
	This sheet has been relabeled as C1.1.

1. Foundation plan for Boat Storage Building 2442 is now labeled S2.1.

2. Coordinates will be added by engineering staff.

3. Non awarded options have been deleted.

	5
	Dwg S.??
	Seem to be missing all structural sheets showing structural framing. You need to submit a complete all in one package, even though you may be using a vendor for the building . 
	Sht. F1.1, Bldg. 2440 Flr. Framing Plan added to package. Further details to be added to package.

	6
	Dwg C 2.1
	Repeat Comment – Have you obtain NASA concurrence to connection the POV lot to Lower Gainsville road?

This drawing is labeled as “Overall Drainage Plan.”  Normal practice is to show the new contour lines.

Provide the full description of the Benchmark to be used the construction of this project, both vertical and horizontal controls.
	Broadmoor has received an email from Paul Mullins dated March 5, 2009, indicating approval.

Contour lines and benchmark data to be added by engineering staff.

	7
	Dwg C 2.2
	Please clarify the various diagonal lines. Do they represent drainage swales? If yes don’t we need a construction detail?

Repeat Comment: Change the enclosure around the trash dumpster. For durability make the fixed wall CMU block, match color and type use on the buildings.  Entrance way should be swing and lockable metal gates, either solid painted steel or galvanized chain-link fence with privacy slats.  
	Clarified on symbol schedule Sht. C1.0. Construction details provided on Sht. C2.1.

Dumpster enclosure revised as per comment.

	8
	Dwg C 2.3
	The fence line crosses the compound entrance driveway. Need to show and specify a gate. Is it double swing or sliding?  Does it need to be automated?  Do we need a badge swipe and video camera connected to the Main SBT 22 quarter deck?
	A gate with all accessories will be provide in accordance with recently received UFC. Video camera to be building mounted.

	9
	Dwg C 2.4
	All these details need the appropriate labeling bubble indicate the detail number, the from sheet and the to sheet (this sheet).
	Corrected by designer.

	10
	Dwg C 3.1
	The abbreviations used on this sheet needs to be on the Civil Title sheet. The details on sheet C 3.2 need section cut bubbles from this sheet.
	Corrected by designer.

	11
	Dwg C 3.2
	All these details need the appropriate labeling bubble indicate the detail number, the from sheet and the to sheet (this sheet).

The Legend on this sheet needs to be on the Civil Title sheet. 
	Corrected by designer.

	12
	Dwg C4.1
	Label the sidewalk that surrounds the Boat Storage Building.
	This sidewalk is being deleted beyond building personnel entrances.

	13
	Dwg  S 1.1
	Show section cuts on the plan view with corresponding details on this sheet.
	Corrected by designer.

	14
	Dwg  S 1.2
	Bollard Detail:  Where is this detail used in plan view? Add a Detail bubble to the label line similar to how you labeled Section A and B.

If this is protecting some structure from vehicle impact, suggest you increase the height to 4-5 ft to make sure it is visible from the backing maneuvers of the large SBT-22 vehicles (large pickups and Vans.)
	Corrected by designer.

Bollard detail corrected as per recent review meeting discussion.

	15
	Dwg  S 2.1
	Bollard Detail:  Where is this detail used in plan view? Add a Detail bubble to the label line similar to how you labeled Section A and B.

If this is protecting some structure from vehicle impact, suggest you increase the height to 4-5 ft to make sure it is visible from the backing maneuvers of the large SBT-22 vehicles (large pickups and Vans.)
	Corrected as per Item No. 14 above.

	16
	Dwg A 1.1
	The shower area needs a drying area with benches and towel hangers as you exit the shower. Appears that you may have to delete 2 cages to make this happen.

Many abbreviations on the see that should be displayed on Architectural Title sheet – see comment #1.
	Shower area revised as per recent review meeting discussion.

Corrected by designer.

	17
	Dwg A 1.1 Second
	Sheet should be A 1.2.

Add term EWC to legend.

Does the Coffee counter in the hallway include a sink and garbage disposal?

For the counter in the River Ops Control Room, please indicate the inclusion of slots spaced evenly apart to allow the pass through of computer power cords and other connection cords.
	Corrected by designer.

Corrected by designer.

Yes, corrected by designer and I.D. staff.

Corrected by designer and I.D. staff.

	18
	Dwg A 1.3
	The bottom have of the Section A label bubble have the numbers reversed. The left side indicates the from sheet and should list A1.1, A1.2 and the right side indicates the to sheet and should list A 1.3.
	Corrected by designer.

	19
	Dwg A 1.4
	Add a detail bubble to the section label line that provides a section number or alpha designation and show the from and to see sheet.
	Corrected by designer.

	20
	Dwg A 1.6
	The elevation views on the building should be showing a rain gutter and down spout system for handling the rain fall off the roofs.

The label for the bollards should include the standard detail bubble, with the top half indicating the detail number on sheet where the detail is shown, the bottom left half indicating the from sheet (A 1.6), and the bottom right half indicating the to sheet (C 1.3).  Also per my previous comments the height needs to be 4-5 feet tall in order to be seen from the larger SBT22 vehicles, while backing.
	Designer coordinating gutter  and downspout system with Met. Bldg. provider.

Corrected by designer.

	21
	Dwg 1.7
	There is a disconnect between this sheet and the architectural roof plans sheet, as to whether the exit stairs have a covered roof.
	Covered roof to be indicated on all appropriate drawings.

	22
	Dwg A 1.10
	Make the following changes /improvement to the design:

For the first floor male shower – Per my comments at the CDW provide an entry area to the shower that provides an area for users to both undress and to dry post shower. This area should be large enough to support at least 50% of the occupancy of the shower. It should have a continuous bench along the wall and multiply hooks for hanging clothing and towels.

Inside the shower area, what is the purpose of the hook adjacent each shower head? Instead of the hook, provide at each shower head a small stainless steel shelf for placing personal shower items like shampoo bottles, soap bars or body soap bottles, etc.

In all restrooms (Heads) provide a seat protector dispenser behind each toilet. Inside each toilet stall provide a hook to hang jackets. Near the entrance door provide a stainless steel shelf to place items a person may be carrying, such as file folder, clip boards, drinks, etc.

I expect better performance from your designer on these types of details. Even your Design QCM should be able to pick up on these types of items. I should not have to police you to provide a quality product you can be proud of. 
	Shower and restroom details to be revised in accordance with discussion at recent review meeting to include the changes/improvements indicated.

	23
	Dwg A 1.?
	Sheet following A 1.10 is the roof plan for the combined Operations and Maintenance buildings, but is mislabeled in the vertical title block. Looks like sheet number should be A 1.11.
	Corrected by designer.

	24
	Dwg E 1.0
	Nicely done electrical discipline title sheet. Good layout and very comprehensive. Good Job!!!
	Response by others.

	25
	Dwg E 2.1
	Recommend adding a double head fixture (a fixture on opposite side of the pole) to the F11A light pole near the pedestrian walkway between the parking lot and the Riverine Compound.
	Response by others.

	26
	Dwg E 4.1
	Need to increase the number of outlets in the walls around the perimeter of the SEAL cage room. Need both for now with access from the rear of the cages. Also go for the future in case the room’s occupancy is changed.

Need a NP outlet in the Armory. Need a NP and SP outlet in the CSS office.
	Response by others.

	27
	Dwg E 4.2
	I don’t see any NP or SP outlets on the second floor. Coordinate with the occupant to determine the best placement and provide an adequate number per the RFP and to provide coverage throughout the floor.
	Response by others.

	28
	Dwg P 1.1
	Where is the grease interceptor for the trench drain and where is the associated piping?  Is this to be shown on the P-drawings or the C-drawings?
	Response by others.

We will also indicate these items on our “C” sheets.

	29
	Dwg P 1.2
	Does the hallway coffee counter need a sink and disposal? 
	Response by others.

See Item #17 above.

	30
	Specs
	Section 01331N, paragraph 1.7.1 of the RFP requires the submitted design specification to be in the current CSI Masterformat. As such, you need to meet the current specification numbering scheme indicated on the Whole Building Design Site and on the CSI website (http://www.csinet.org/s_csi/sec.asp?TRACKID=&CID=5&DID=5)
	Specifications to be revised to Specsintact system as per discussion at recent review meeting.

	31
	Specs
	General Comment: Many sections in this submittal are out of order, making review difficult. This also shows a poor Design Quality Control. Please correct at the next submittal.
	Specifications to be revised to Specsintact system as per discussion at recent review meeting.

	32
	Specs
	Section 02300, paragraph 3.17 makes reference to a Division 2 Section covering sub-drainage. That section is not included.
	Specifications to be revised to Specsintact system as per discussion at recent review meeting.

	33
	Specs
	Section 02300: paragraph 3.22 refers to “owners property.” Change that to indicate “Station.”  

Regarding any project requirements indicating soil to be obtain or disposed of, do not indicate availability from the station or that the station is a place of disposal. All import shall be from off station and all export shall be to off station.

Regarding the language in sub-paragraph B, that the Architect shall direct consider the following:

· While the design and construction is internal to your organization, how much involvement do you want the architect to provide?

· If you are allowing the Architect or Design of Record  to provide direction to the construction crew, consider that any direction that changes contract time or cost can only come from the Contracting Officer and if such direction is given without the Contracting Officer involvement it will be at your own risk and cost.
	Specifications to be revised to Specsintact system as per discussion at recent review meeting.

	34
	Specs 
	Sections 81113, 84113, and 85113 all need to indicate a compliance of doors, window, amd their frames to ATFP blast loads, as prescribe by the RFP.
	Specifications to be revised to Specsintact system as per discussion at recent review meeting.

	35
	Calcus
	The calculations are now much more complete and thorough. However they are still missing key Civil Engineer calculations showing hydrology and drainage structures capacities. Include these and the calculations from the building vendor showing structural members and column foundation loading at the pre-final submittal. Failure to submit a complete package will be grounds for rejection.
	Additional / complete calculations will be provided at the pre-final submittal.

	36
	Design Pkg
	The Design Quality Control Manager need to thoroughly review the entire design submission package to ensure it is complete, meets UFC and RFP requirements, and to look for inter-discipline coordination errors.
	The DQC will comply with UFC / RFP requirements.

	37
	Annotated Comments
	I did not receive the annotated comments from by concept design review.  This is standard practice and professional courtesy to answer my comments from the previous submit at each submittal stage. Again failure to do so at the pre-final will be cause for rejection. 
	Response to comments from concept design review forwarded on March 2, 2009.


