SOV RIVERINE AND COMBATANT

CRAFT OPERATIONS FACILITY
8.749 Acre Parcel

Located at

John C. Stennis Space Center

Hancock County Mississippi

Hydrology Study

April 6, 2009

Prepared by:

Dammon Engineering 

1095 Florida Avenue

Slidell, La. 70458

985-649-5832

dammonengineering.com
SOV RIVERINE AND COMBATANT

CRAFT OPERATIONS FACILITY
8.749 Acre Parcel

Located at

John C. Stennis Space Center

Hancock County Mississippi

Hydrology Study

April 6, 2009

Prepared by:

Dammon Engineering 

1095 Florida Avenue

Slidell, La. 70458

985-649-5832

dammonengineering.com


[image: image1.wmf]607


SOV RIVERINE AND COMBATANT

CRAFT OPERATIONS FACILITY
8.749 Acre Parcel

Located at

John C. Stennis Space Center

Hancock County Mississippi

SITE DESCRIPTION

The property is bounded by Lower Gainesville Road on the North, Endeavour Blvd. on the East, the Pearl River on the East, and by the East Pearl River Canal South of the Parcel.

CURRENT DRAINAGE

The property has several peaks and valleys with a variety of contours throughout the site that allow drainage into the East Pearl River Canal at the South end of the site.

STUDY METHODOLOGY

The modified rational method was used to determine peak flows for the 10-year storm event for the limits of construction, both prior and post-development.

The swales were designed using the modified rational method for a 10-year storm event. The expected rainfall intensity was taken from Data Book for Civil Engineers Vol. 1 1960, Fig. “B” pg. 18-01 (Seelye).

The runoff from areas not serviced by a swale do not require any detention because prior and post development runoff patterns remain in place. Therefore no calculations for these areas were performed. 

PROPOSED DRAINAGE

The bldg elevations are set at 16.00’ and the end invert drain is set at 8.50’. On-site drainage swales are designed for a 10-year storm event and flow into an 18”x29” arch outlet pipe.

Rainwater shall run off the roofs into the gutter system and into the down spouts. Once in the down spouts water shall run onto the concrete aprons which will direct the water to the center and sides of the concrete aprons allowing the water to flow into the swales and out to the East Pearl River Canal as designed.

Improvements to the existing ditch that runs along the western limit of construction (gravel road) will preserve the natural drainage pattern and provide adequate drainage for the site development not serviced by the new swale. 

Property to the north of the development will retain ponding characteristics post-development. All pond water created by the grading of the site will drain into an 8”CMP which is connected to the site swale that discharges into the East Pearl River Canal.

SUMMARY OF CALCULATIONS

Existing grounds area = 
8.749 acres, C=0.15
Tc=75.12 min.

Post-Development Area into swale:

Parking lot, Buildings=  
2.495 acres, C=0.90                         
Tc=31.80 min.

Green space=
2.087 acres, C=0.15
Tc=31.80 min.

Offsite Ponding=    
0.567 acres, C=0.15
Tc=19.04 min.

Note:  Remaining 4.167 acres sheet flows into existing drainage pattern which discharges into the East Pearl River Canal.

OVERALL SITE CALCULATIONS

[image: image2.jpg]STENNIS RIVERINE
STORMWATER RUN-OFF CALCULATIONS

PROJECT:

Formulas used:
[1] RATIONAL METHOD: Q=Aci

iwhere: Q= Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm
assumed.

Area of watershed in acres.

Coefficient of run-off [2].

Intensity of rainfall in inches per hour based on concentration time. [3]

) 07
e= ™)
(1140(s
jwhere: TC= Time of concentration= time required for rain falling at most remote point to reach
discharge point.

c=  Site run-off coefficient based on conditions shown.
Percent slope of overland flow.
AREA OF WORK - PRIOR DEVELOPMENT
10 Year Frequency

0 0.000 Acres

10000 0230 Acres

371109 8.519 Acres

381109 sqft 8.749 Acres

run-off length ft Elev diff= 6

0.15 run-off coef
0.7407 percent slope
itherefore TC=D= 7512 minutes
Expected rainfall
intensity i= 3.15 infhr

AREA OF WORK - POST DEVELOPMENT
10 Year Frequency

130390

2.993 Acres

10000 0.230 Acres

240719 5.526

381109

8.749 Acres

Runoff length ft

c= 041 Runoff coef
= 0.5208 Percent Slope
therefore TC=D= 36.12 minutes or

and from Rainfall
in/hr

1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02

3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01

4. Chen, W.F. The Civil Engineering Handbook. 1995. Thl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eg.# 28.32, pg. 969





CALCULATIONS FOR WATERSHED 

SERVICED BY NEW SWALE AND OUTLET PIPES

[image: image3.jpg]STENNIS RIVERINE
STORMWATER RUN-OFF CALCULATIONS

PROJECT:

[1] RATIONAL METHOD: Q=Aci

Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm
assumed.

Area of watershed in acres.

Coefficient of run-off [2].

Intensity of rainfall in inches per hour based on concentration time. [3]

(]_SS{'““O " 9}9-7)

(1140(s%5Y)
Time of concentration= time required for rain falling at most remote point to reach
discharge point.
c=  Site run-off coefficient based on conditions shown.
s=  Percent slope of overland flow.
WATERSHED SERVICED BY DRAINAGE SWALE - POST DEVELOPMENT
10 Year Frequency

[4] TC=

TC=

Q, = Aci
\Watertight Surfaces
. )= I
Gravel Surface 0
c2) =
Green Space
3=

108688

94492 sqft =

Summary 203180 sqft=
s

Duration (D) = Time of concentration (TC)

where L = 960 run-off length ft Elev diff= 6

c= 0.55

S= 0.6250
therefore TC=D= 32.09
Expected rainfall

intensity i= 315

run-off coef
percent slope
minutes

in/hr

DISCHARGE END AREA REQUIREMENTS
10 Year Frequency
Area requirements for pipe servicing swale located in Zone #1 of the corresponding Key Plan

]

(cy/@eh)

[5] A=

Discharge Area required
Acceleration of gravity
Discharge coefficient
Hydraulic head
Flow volume from run-off
Pipe #1: Servicing swale located in Zone #1 of the corresponding Key Plan.
1.380 cfs
0.62 coefficient
32.16 ft/ft/sec

3.80

inch diameter
Pipe #2: Servicing all zones shown in the corresponding Key Plan.
8.099 cfs
0.62 coefficient
32.16 ft/ft/sec

REQUIRED CONDUIT = inch diameter










_1297847803.dwg

