SOV RIVERINE AND COMBATANT

CRAFT OPERATIONS FACILITY
Located at

John C. Stennis Space Center

Hancock County Mississippi

BLDG. 2440/2441

EXTERIOR WALL THERMAL RESISTANCE REPORT

March 13, 2009

Prepared by:

Dammon Engineering 

1095 Florida Avenue

Slidell, La. 70458

985-649-5832

dammonengineering.com

SOV RIVERINE AND COMBATANT

CRAFT OPERATIONS FACILITY

Located at

John C. Stennis Space Center

Hancock County Mississippi

CLIMATE ZONE AND MINIMUM INSULATION REQUIREMENTS

Project is located in Hancock County, Mississippi. Climate Zone 2A, minimum insulation value for mass walls above-grade R-5.7, maximum U-factor U-0.151.

DESCRIPTION OF EXTERIOR WALL COMPONENTS

Bldg. 2440 Operation Facility / 2441 Maintenance:

Exterior walls are continuous 8” concrete block masonry from first floor to eave height, top of masonry = 24.0’. The perimeter of the building shall have a 4” spilt-face concrete block veneer 6’ in height. 

A wall system of low-density CMU blocks, polyisocyanurate rigid board insulation, and air spaces are used to achieve the required assembly minimum thermal resistance. See details below.


[image: image1.wmf]SPLIT-FACE VENEER DETAIL


1. R-1.3: Medium density (115 lb./ft^3), 4” Split-face concrete block veneer. Includes standard air film resistances. (ASHRAE 90.1-2007 TBL. A3.1B)

2. R-9.3: 1” thick Dyplast Shield( Cavity Wall Insulation with reflective surface and 1” dead air space.  (http://www.dyplastproducts.com) 

3. R-2.4: Low density (85 lb./ft.^3), 8” CMU wall grouted at vertical and horizontal reinforcement, remaining cells empty. (ASHRAE 90.1-2007 TBL. A3.1C)

 
[image: image2.wmf]CMU WALL DETAIL


1. R-12.8: 2” thick Dyplast Shield( Insulation with reflective surface. (http://www.dyplastproducts.com)

2. R-2.4: Low density (85 lb./ft.^3), 8” CMU wall grouted at vertical and horizontal reinforcement, remaining cells empty. (ASHRAE 90.1-2007 TBL. A3.1C)

3. R-1.4: 3/8” channel (R-0.82) fastened to CMU wall, 5/8” gyp. board (R-0.56) fastened to channels. (Values for air space created by channel and gypsum board taken from ASHRAE 90.1-2007 TBL. A9.8A and TBL. A9.4D respectively)

SUMMARY

Minimum insulation value, and maximum U-Factor value requirements for exterior above-grade walls have been met and exceeded.

8” CMU wall with 4” split-face veneer:

Minimum: R-5.7
Provided: R-13

Maximum: U-0.151 
Provided: U-0.08

8” CMU wall with metal panel exterior finish and gypsum board interior finish:

Minimum: R-5.7
Provided: R-16.6

Maximum: U-0.151
Provided: U-0.06

_1298446527.dwg

_1298448283.dwg

