	PROJECT REVIEW
COMMENTS

	Project No.  0LA2083
	     Agency:     USMS
     Realty PM:  Sylvia Cabello

	
	Location:   Kenner, LA
	Building Name:

	
	Review Phase:    95% CD Review
	Date: 3/29/2012
	Page 1 of 2

	Reviewer: D. WONG
	Organization: GSA 

	Comm.

No.
	page No.
	COMMENTS

ARCH__ CIV __ STRC __ MECH      ELEC _X_FIRE __  OTHER ___
	RESOLUTIONS (BY A/E)

	 1
	 E-1
	REFERENCE TO LIGHTING FIXTURE SCHEDULE, LIGHTING FIXTURE TYPE L: FOR ENERGY SAVING PURPOSE; RECOMMEND USE FLUORESCENT LIGHTS IN LIEU OF INCANDESCENT LIGHTS.
	A energy efficient lamp has been selected.

	 2
	 E-1
	DO NOT RECOMMEND INSTALL SUITE 13 POWER PANEL IN JANITOR CLOSET. 
	Power panel moved to warehouse.

	 3
	 E-1
	RECOMMEND PROVIDE PANELBOARDS IN ELECTRICAL ROOM. LIGHTINGS AND OUTLETS IN ELECTRICAL ROOM SHALL BE ON EMERGENCY CIRCUITS.
	Power panel moved to warehouse.

	 4
	 E-1
	REFERENCE TO ROOM P1, ELECTRICAL NOTE 1: SHOW CIRCUIT NUMBER FOR LAMPS ON EMERGENCY CIRCUIT. 
	Amended comment.

	 5
	 E-1
	PLEASE CLARIFY THAT EXISTING METER BANK SHALL BE REMOVED OR REMAIN.
	Amended comment, existing meter bank to remain.

	 6
	 E-1
	REFERENCE TO ELECTRICAL NOTE #5: CLARIFY THAT WHETHER PUSH BUTTON IS REQUIRED FOR PROJECTOR SCREEN, IS SO, PLEASE SHOW ON FLOOR PLAN.
	A manual projector screen will be installed.  Comment removed reference to power.

	 7
	 E-1
	CORRECT KVA LOAD FOR THE FOLLOWING CIRCUITS: SHITE 13 CKT 37, SUITE 13 CKT 28, MDP CKT 7, ATS CKT 11 AND ATS CKT 13.
	Amended drawing.

	 8
	 E-1
	REFERENCE ROOMS TO P20 AND P21: 
(1) CIRCUIT MDP-6,8 IS SHOWN SERVING VVT-2, HOWEVER, SAME CIRCUIT IS SHOWN SERVING EF-6 ON PANELBOARD SCHEDULE. PLEASE RESOLVE DISCREPANCY.
(2) CIRCUIT MDP-6,8 IS SHOWN SERVING EF-6 IN ROOM C2. THIS COMMENT IS IN CONJUNCTION OF COMMENT (1) AS SHOWN ABOVE.
	Amended drawing.

	 9
	 E-1
	REFERENCE ROOM TO P22: CIRCUIT MDP-9,11 IS SHOWN SERVING VVT-3, HOWEVER, SAME CIRCUIT IS SHOWN SERVING OUTLETS AND RTU’S ON PANELBOARD SCHEDULE. PLEASE RESOLVE DISCREPANCY.
	Amended drawing.

	 10
	 E-1
	MEP-9 IS SHOWN SERVING DUPLEX RECEPTACLES IN ROOM C2. THIS COMMENT IS IN CONJUNCTION OF COMMENT #9.
	Amended drawing.

	 11
	 E-1
	MEP-11 IS SHOWN SERVING DUPLEX RECEPTACLE IN ROOM P20 AND P21. THIS COMMENT IS IN CONJUNCTION OF COMMENT #9.
	Amended drawing.

	 12
	 E-2
	REFERENCE TO ATS PANEL: CIRCUITS ATS CKT 19,21 AND ATS CKT 31,33 ARE NOT SHOWN ON FLOOR PLAN. THIS COMMENT IS IN CONJUNCTION OF COMMENTS #8 AND #9.
	Amended drawing.

	 13
	 E-2
	REFERENCE TO CMPTR PANEL: CIRCUITS #5, #7 AND #11 ARE NOT SHOWN ON FLOOR PLAN.
	Amended drawing to reflect these circuits.

	 14
	 E-2
	REFERENCE TO ELECTRICAL SITE PLAN:

(1) SHOW SECONDARY FEEDER FROM POLE MOUNTED TRANSFORMERS UNDERGROUND TO BUILDING.

(2) CLARIFY THAT WHETHER SECONDARY FEEDER SHALL BE PROVIDED AND INSTALLED BY ELECTRICAL CONTRACTOR OR BY UTILITY COMPANY.

(3) CLARIFY THAT WHETHER POLE AND POLE MOUNTED TRANSFORMER SHALL BE PROVIDED AND INSTALLED BY ELECTRICAL CONTRACTOR OR UTILITY COMPANY.

(4) SHOW KVA RATING, PRIMARY AND SECONDARY VOLTAGE, NUMBER OF PHASE, NUMBER OF WIRE ETC. OF TRANSFORMERS. 
	Amended drawing.

	 15
	 E-2
	REFERENCE TO ELECTRICAL RISER DIAGRAM:
(1) LOCATE NEMA 3R JUNCTION BOX ON SITE PLAN OR/AND FLOOR PLAN. 

(2) PROVIDE CONCRETE PAD FOR GENERATOR.

(3) SHOW POWER FACTOR OF GENERATOR.
	Amended drawing. Generator now shows a slab on grade.  The power factor of generator has been added to the note.

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


