	PROJECT REVIEW
COMMENTS

	Project No. 0LA2083
	Agency:     USDA-APHIS
Realty PM:  Sylvia Cabello

	
	Location: Keener, LA
	Building Name: 

	
	Review Phase: 95% CD Review
	Date: 04/02/2012
	Page 

	Reviewer: Kenneth Kwan
	Organization: GSA – 7PCE 

	Comm.

No.
	page No.
	COMMENTS

ARCH__ CIV __ STRC __ MECH  x  ELEC __ FIRE __  OTHER ___
	RESOLUTIONS (BY A/E)

	1
	M-1
	Mechanical Plan.

Reduce exhaust air from Women Restroom and Men Restroom to minimum of 140 cfm (EF-2 & EF-3 each) as required, so minimum outside air from Rooftop Unit RTU-1 could be kept at minimum.  Also, supply air to these rooms should be reduced to that below of the exhaust air.   

	Drawing amended

	2
	M-1
	Rooftop Air Conditioning Unit Schedule.

Change and increase Min. OA for RTU-1 to match the total exhaust air from EF-1 thru EF-4, to avoid negative pressure in building.     

	RTU #1 and #2 supply air to the general areas and make up air is split between these two RTU’s.

	3
	M-1
	Fan Schedule.

Change exhaust fan EF-8 exhaust air cfm from 400 to 500, to match supply air to room as shown.   


	Drawing amended

	4
	M-1
	Fan Schedule.

Change exhaust air cfm for exhaust fans EF-2 & EF-3 per Comment No. 1 above.


	Drawing amended

	5
	P-1
	Water & Sanitary Sewer Plan.

Provide and indicate the water supply pipe to Rooftop Unit RTU-2 for make-up water of steam humidifier in unit.  

	Drawing amended

	
	
	
	

	
	
	---- End of Comments -----
	

	
	
	
	


