INTERNATIONAL BUILDING CODE 2006 REQUIREMENTS

SLIDELL MEMORIAL HOSPITAL 

ER ENTRANCE MODIFICATIONS

JOB # 1939

Occupancy Classification:
Institutional, Group I-2. (Sec 308.3).

Occupant Load: (TBL 1004.1.1)
Inpatient treatment areas = 240 Gross sq. ft. / occupant.

Outpatient areas = 100 Gross sq. ft. / occupant.

No new area to be constructed, existing occupant load to remain.

Exit Access Requirements: (Sec 1019)
2 exits required for 1 – 500 occupants in institutional occupancy. (6+ exits provided).

Exit access travel distance = 200’ sprinkled (Table 1016.1).

Allowable height and bldg. Area: (TBL 503)
I-2 = 15,000 s.f. / 2 story allowed, no change to existing s.f. this project. Note: Section 506.3, Automatic sprinkler system increase allows 300 percent increase with for a building with no more than one story above grade.

22,500 existing s.f. provided / 2 story.

Construction Classification: (Sec 602.2)
Type IIA

Fire Resistance Rating Requirements for Building Elements: (TBL 601)
Structural Frame = 1 hrs.

Bearing Walls (interior and exterior) = 1 hrs.

Non-Bearing Walls = 0 hrs.

Floor Construction = 1 hrs.

Roof Construction = 1 hrs.

Note: Existing sprinkler system is allowed as a substitution for fire rating.

Fire Resistance Rating Requirements for Exterior Walls: (TBL 602)
All exterior walls are existing.

Fire Alarm System Requirements: (Sec 907)
This existing building has a fire and smoke system in place.

Fire Protection System Requirements: (Sec 903)
This existing building has a sprinkler system in place.

Construction Documents: (Sec 1603)

This (existing) Bldg. shall be designed in accordance with IBC Section 1609 as a fully enclosed Bldg. using the following information:

Basic Wind Speed (3 second gusts) = 130 mph (Fig 1609)

Importance Factor: Category III Bldg., IE = 1.00, IS = 1.o, IW = 1.00 (TBL 1604.5)

Exposure B, determination of wind loads shall be in accordance with IBC Sec 1609.4

Minimum live loads shall be determined in accordance with TBL 1607.1

Ground snow loads = 5 psf (Fig. 1608.2)

Based on the survey of this property by J. B. Burkes & Assoc., Inc.

This property is in a Special Flood Hazard Area.

F.I.R.M. Community Map No. 220204 0010 C

Date: 4/21/1999

Flood Zone: AE

Base Flood Elevation = 12.0’.

