DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

December 15, 2010

To: 
Mr. Mike Palermo


K.B. Kaufmann 


3173 Terrace Ave. East


Slidell, LA 70458

REF: Patterson Dental Supply


107 Mallard Street


Saint Rose, LA 70087

Dear Mr. Palermo,

The Louisiana State Fire Marshal has reviewed your project and indicated that there is a deficiency regarding the required separation distance of exits for the Business area. 

NFPA 101:38.2.4

“Two remotely located exits are required from Business area. Minimum distance between them, measured from closest jambs, shall be ½ the maximum diagonal length of space or area.”

The calculated minimum separation distance for these exits is 84'-0”. Currently there is only  72'-0” of separation between the existing two front entrances. To satisfy this code we propose adding an exit door to the corridor located adjacent to the Branch Manager office at the SouthEast corner of the business space. 

Sincerely,

Chuck Dammon

Dammon Engineering

Attachments:

1. Revised Floor Plan

