STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana  70806
225-925-4920

H “BUTCH” BROWNING
FIRE MARSHAL

I N F O R M A T I O N  R E Q U E S T
N O T   -   F O R   -   P E R M I T T I N G

ROBERT WILTSE
DAMMON ENGINEERING INC
554 OLD SPANISH TRAIL
SLIDELL, LA  70458-0000	RE:  P0411705
DENTAL OFFICE FOR DR JONES
7240 CROWDER BLVD
NEW ORLEANS,     70127

NFPA 101, 2009
IBC, 2009 (CHAPTERS 9 & 10)

AMBULATORY CARE
BUSINESS

Dear Applicant:

Additional information is required to perform a proper review.  The project referenced above is being held pending submission of the following information:

1.	RS 40:1574 and/or RS 40:1730.39.A  Additional drawings and/or specifications are required:

	a)  Provide REVISED DRAWINGS that indicate nitrous oxide stations at NOT MORE THAN THREE (3) patiient stations.  If nitrous oxide is provided at four (4) or more stations the project will be reviewed as an Ambulatory Health Care occupancy. 
	
2.	NOTE:  Please mail all correspondence related with this project to:

	NEW ORLEANS PLAN REVIEW
	Office of State Fire Marshal
	1450 Poydras St.
	Suite 1500
	New Orleans, LA   70112
	
Contact the reviewer at 504.568.8509 (fax: 504-568-8511), if you have any questions regarding this project. 

3.	NOTE: Please ENCLOSE A COPY OF THIS LETTER WITH FUTURE SUBMITTALS OR OTHER CORRESPONDENCE pertaining to this project. 

Due to the lack of information, the referenced project has NOT been reviewed.  Please direct the requested information to my attention.  Processing will continue upon receipt of the information requested above.  Enclose a copy of this letter with future submittals and/or other correspondence pertaining to this project.

This project will be returned as "NOT IN COMPLIANCE" if the requested information is not received by this office within 21 days of the date of this letter, thereby requiring a RESUBMITTAL of the entire project along with a new completed application and appropriate review fee.

CONSTRUCTION IS NOT AUTHORIZED until a satisfactory review has been performed and a formal review letter has been issued by this office.

REVIEWED BY:
JULIE LITTLE
ARCHITECT

CC:
Grace Tama Development Co Inc
Bhola Dhume
New Orleans Fire Department*
New Orleans District*     5045688506