[image: image1.jpg]IDAMMON

ENGINEERING | NLC.

J  Archiltectls & Engineers




554 Old Spanish Trail
Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net


7-29-13
David Luparello
Dapco

59118 N Pearl Dr.

Slidell, La. 

Ref: Laquinta Inn 

        Gonzales La.

Per our inspection today along with Jack Kennedy of Jefferson Sprinkler, we noted some sprinkler heads that need to be replaced along with some escutcheon plates that are missing and a leak.
1) Room 403, change out 2 sprinkler heads
2) Hallway near room 401 change out sprinkler head

3) Room 401, sidewall sitting area change out sprinkler head

4) Room 301, sidewall area change out sprinkler head
5) Rear stairwell, change out sprinkler head at landing

6) Room 301, change out sprinkler head on sidewall

7) Room 304, check proper coverage/distance from door to window

8) Room 315, change sprinkler head in bathroom

9) Room 321, sprinkler head is crooked

10) 2nd floor linen storage room, change out one sprinkler head and raise one sprinkler head to proper height

11) Room 201, change out 2 sprinkler heads

12) Rear stairwell valve leaking around plug, change out sprinkler head under stairwell

13) Room 101, change out sprinkler head in arch

14) Room 102, change out 2 sprinkler heads and adjust one to fit hole

15) Room 103, sidewall sprinkler head deflector is bent change out
16) Room 106, change sprinkler head

17) Hallway outside of Jambalaya, room raise sprinkler head to proper height

18) Guest laundry room, change sprinkler head 

19) Front desk area, change sprinkler head
20) Kitchen area, install escutcheon plates

21) Dining area A/C closet, install escutcheon plates

Chuck Dammon
V/P Project Manager

Bill Kingsmill’s contact information is as follows:
William Kingsmill (kingsmillprop@bellsouth.net)
Cell: (504) 528 3838
1200 Business Highway 190, Suite 13
Covington, LA 70433
 
Lawrence Wm. Haik, Sr
Republic Commercial Properties, LLC                
1539 Royal Palm Dr.
Slidell, LA 70458
(985) 960-7033
 
