
SECTION 15430PRIVATE 


PLUMBING SPECIALTIES
PART 1  GENERAL

1.1
SUMMARY


A.
Provide floor drains, Floor Sinks, Cleanouts, Wall Hydrants, Trap Primers, Grease Traps as shown on drawings.  

PART 2  PRODUCTS

2.1
FLOOR DRAINS (FD)


A.
Laundry Rooms: J. R. Smith 2005‑A6‑B‑P.


B.
Mechanical & Fire Pump Rooms: J. R. Smith 2220‑P.


C.
Toilet Rooms: J. R. Smith 2005‑A6‑B‑P.


D.
Showers ‑ J. R. Smith 2005‑A6‑B‑P.


E.
Food Prep: J. R. Smith 3040‑P


F.
Manufacturers:



1.
Josam



2.
Wade



3.
Zurn



4.
Approved substitute


G.
Provide trap primers on all floor drains.

2.2
FLOOR SINKS (FS)


A.
Food Prep: J. R. Smith 3100‑94‑P


B.
Manufacturers:



1.Josam



2.Wade



3.Zurn



4.Approved substitute

2.3
CLEANOUTS


A.
Cleanouts shall be provided where shown on the drawings and shall be the same size as the pipe on which the cleanout is installed.


B.
Cleanouts in vertical piping shall be roughed with centerline not more than 1' 6" above the finished floor, but high enough to clear the baseboard.


C.
Exterior Areas: Cast iron ferrule and countersunk bronze plug, J. R. Smith 4400.  Where not in paved areas, cleanout shall be set in 12" x 12" x 6" deep poured concrete pad set flush with grade.


D.
Interior Finished Wall Areas: Cast iron, extra heavy cleanout tee with countersunk bronze plug tapped for machine screw, shallow stainless steel face‑of‑wall access cover, and vandal‑proof securing screw, J. R. Smith 4472.


E.
Interior Finished Floor Areas: Cast iron with gasket seal threaded plug for easy removal, adjustable round nickle bronze top recessed for tile with securing screw; J. R. Smith 4151.


F.
Manufacturers:



1.
Josam



2.
Wade



3.
Zurn



4.
Schier



5.
Approved substitute

2.4
WALL HYDRANTS (WH)


A.
Manufacturers:



1.
J.R. Smith Model 5509.


B.
Other acceptable manufacturers offering equivalent products.



1.
Arrowhead



2.
Josam.



3.
Wade.



4.
Woodford



5.
Zurn.


C.
Wall Hydrant:  ANSI/ASSE 1019; 3/4" in size, non‑freeze, integral vacuum breaker, self‑draining type with hose thread spout, removable key and bronze box with chrome plated face.

2.5
LAWN HYDRANTS (LH)


A.
Manufacturers:



1.
Woodford Model Y95.


B.
Other acceptable manufacturers offering equivalent products.



1.
Arrowhead



2.
Josam.



3.
J.R. Smith



4.
Wade.



5.
Zurn.


C.
Lawn Hydrant:  3/4" in size, tamper proof cover, non‑freeze, integral vacuum breaker, self‑draining type with hose thread spout and removable key.


D.
Mount hydrant in 14"x14"x4" concrete pad.  Concrete pad shall be flush with grade.

2.6.
TRAP PRIMERS


A.
Precision Plumbing Company Model No. P‑2.


B.
Manufacturers: Approved substitute



1.
Josam



2.
J.R. Smith



3.
Zurn


C.
Automatic type, bronze body with integral vacuum breaker, strainer and union ends.

2.7 LINT INTERCEPTOR (LT)

A. Manufacturers:

1. J.R. Smith 8910-50.

B. Other acceptable manufacturers offering equivalent products:

1. Josam

2. Zurn

C. Construction:  Epoxy coated fabricated steel for fully recessed flush with grade installation, with stainless steel primary and secondary lint screens.  Provide with threaded 2” vent connection, and extension option of field determined height.


D.
Unit Rating:  50 gal/min.

2.8
GREASE TRAP (GT)


A.
Manufacturers:



1.
J.R. Smith 8350.


B.
Other acceptable manufacturers offering equivalent products.



1.
Josam.



2.
Wade.



3.
Zurn.


C.
Construction: Epoxy coated fabricated steel for fully recessed flush with grade installation, with multi‑weir baffle assembly, integral deep seal trap, removable integral flow control, and non‑skid epoxy coated steel cover with gasket and securing handle.  Provide flow control fitting and extension option of field determined height.

D. Unit Rating: 50 gal/min flow and 100 lbs grease capacity.

2.9 LINT INTERCEPTOR (LI)

A. Manufacturers:

1. J.R. Smith 8910-100


B.
Other acceptable manufacturers offering equivalent products.



1.
Josam.



2.
Wade.



3.
Zurn.

C. Construction: Epoxy coated fabricated steel fully recessed flush with floor installation, with primary and secondary stainless steel lint screens.

PART 3
EXECUTION

3.1
PREPARATION


A.
Coordinate cutting and forming of floor construction to receive drains to required invert elevations.

3.2
INSTALLATION


A.
Install in accordance with manufacturer's instructions.


B.
Extend cleanouts to finished floor or wall surface. Lubricate threaded cleanout plugs with mixture of graphite and linseed oil.  Ensure clearance at cleanout for rodding of drainage system.


C.
Encase exterior cleanouts and interceptors/traps in concrete flush with grade.


D.
Install trap primers on all floor drains.


END OF SECTION


15430 - 1
PLUMBING SPECIALTIES

