East Yard

TEXTRON

ADDENDUM  NO. 4
October 13, 2004

1) Addendum No. 2, “SCOPE OF WORK” – Add the following:

“6.
Contractor shall install 1200A new main distribution panel (supplied by Owner) on interior electrical equipment platform.

“7.
Contractor shall provide and install circuits, including local disconnect switches, from new main distribution panel to air compressor skid, refrigerant dryer skid, and HVAC unit.

“8.
Contractor shall provide and install circuits from new main distribution panel to paint rooms (1 & 2) and airblast rooms (1 & 2) supplied by Owner.”
2) Section 16415, Par 2.11, “PANELBOARDS” – 
Add the following text at the end of this section: “Manufacturer: Square D.”
3) Section 16415, Par 2.12.5.a. “Single and Duplex, 20-Ampere, 125 Volt” – 
Delete “Non-locking: NEMA type 5-20R,;” change the remaining text to read ”locking: NEMA type L5-20R complete with UL listed weatherproof cover and box for wet locations.  Hubbell part no. 7580G.”

4) Section 16415, Par 3.8, “NOT USED” – 
Change this section to read “LIGHTING TRANSFORMERS – All lighting transformers shall be dry-type construction for industrial use indoors (i.e. NEMA 12 enclosure) with 115 degrees C rise above ambient.  Transformers shall be provided with full capacity taps, four 2-½% with two above and two below, for rated primary voltage. Manufacturer: Square D.”
5) Section 16415, Par 3.10, “MOTOR CONTROL” – 
Add the following text at the end of this section: “Combination motor starters shall be suitable for industrial use indoors (i.e. NEMA 12 enclosure).”
6) Section 16415, Par 3.11, “MOTOR DISCONNECT MEANS” – 
Add the following text at the end of this section: “Motor disconnects installed outdoors shall be suitable for wet locations (i.e. NEMA 4X enclosure).  Manufacturer: Square D.”
7) Section 16510, Par 2.3, “LIGHTING CONTACTOR” – 
Add the following text at the end of this section: “Manufacturer: Square D.”   
8) Drawings.  Add “Electrical Block Diagram,” Rev 0 dated 10/13/04.
END – ADDENDUM NO. 4
P:\20040125 Textron\2000 S&C\specs\Addendum No. 4.doc

Addendum No. 4 Page 1

