DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

       December 7, 2007
Mr. James Waite

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement

 And Building Safety.

8181 Independence Boulevard

Baton Rouge, Louisiana 70806

RE: PO333142

       Textron Marine – Front Street

       PO334424

       Textron Marine- Office Addition

Dear Mr. Waite

Jim I researched the door swing code again. It clearly states that doors shall swing in the direction of egress travel where serving an occupant load of 50 or more persons or a group H occupancy. We are group B occupancy and our occupant load is only 7.55 persons. Total sq. ft. is 755 / 100 = 7.55 people. Therefore our door can swing in as shown.

Also GA File No. FC 4390 clearly states using ½” wood structural panels only and not calling out for fire rated plywood at the top of the stairs. Therefore no rating is required on any of the top decking. 

Please call me with any question you may have.

Sincerely,

Chuck Dammon

