Calculate a beam to replace a load bearing wall in the residence at 3801 St. Charles Ave. Unit #301

GIVEN: This is a 5 Story building, Red Iron framing with 3” concrete decking.  The load bearing wall is situated between two rooms.  The living room measures 19’-6 ½”  orthogonal to the load bearing wall and the family room measures 9’-6” on the other side of the load bearing wall.  There are 2 floors and a roof above the load bearing wall to support.

w loading for each area:

Lighting					1 psf

Hvac ductwork				2 psf

5/8” Sheetrock ceiling			2.8 psf

Metal decking for concrete		2.5 psf

3” concrete	floor	3/12 * 120 pcf  =	30 psf

Hardwood floor				4 psf

Each C-channel is approximately 24” o.c. so the area supported by each C-channel is approximately 24” wide x 12” along the C-channel:

42.3 psf x 2’ x1’ = 84.6 plf

Assumption : 10” C-channel weights approx. 7 plf

Adding these together we get 84.6 plf + 7 plf = 91.6 plf along each C-channel

The DEAD LOAD from each C-channel supported by load bearing wall =

[(19.5’ / 2) + (9.5’ / 2)] x 91.6 plf = 1328.2 #  (1.3k)

LIVE LOAD on each C-channel @ 40 psf =

[(19.5’ / 2) + (9.5’ / 2)] x 2s.f. x 40psf = 1160 #  (1.2k)

LRFD Loads 	1.2 D + 1.6 L

[(1.3k x 1.2) + (1.2k x 1.6)]  =  3.48 k @ 24” o.c.

Also include the dead loads from the load bearing walls on the 4th and 5th floors

(9’ x 2’ o.c.) x 10 psf  =  180 #/24” o.c.     (.2k @ 24” o.c.)

.

Total load from load bearing wall 3.68k  @ 24”o.c.

Length of load bearing wall  =  13’-2”  (13.2’)

.

Deflection Limit  Δ =  (13.2’ x 12”/ft)  /  360  =  0.44”

w from 3rd , 4th and 5th ceiling loads

w= 3.68k  x  3  = 11.04 k @ 24” o.c.

For I use unfactored w

Imin = 5 x (8.1/2) x (13.2)4 x 1728 / (384 x 29,000 x .44)

Imin  =  216.8 in4

= (11.04/2) (13.2)2 /8  =  120.2 ft-k

= (11.04/2) (13.2)  / 2  =  36.43k

= 120.2 ft-k  x 12 “/ft   / (.9x50ksi)   32.5 in3

Wide Flange Options:

W8x58	A = 17.1,	d=8.75,	tw = 0.510

Ixx = 228 > 216.8		Zxx = 59.8 > 32.05

W10x45	A=13.3, 	d=10.1,	tw = 0.350

Ixx = 248 > 216.8		Zxx = 54.9 > 32.05

W12x30	A=8.79, 	d=12.3,	tw = 0.26

Ixx = 238 > 216.8		Zxx = 43.1 > 32.05

W14x26 	A=7.69, 	d=13.9,	tw = 0.255

Ixx = 245 > 216.8		Zxx = 40.2 > 32.05

Check Shear

W8x58  = 8.75x.51x50=223k  > 36.48k

W10x45 = 10.1x.35x50=176.7k  >36.48k

W12x30 = 12.3x.26x50=159.9k  >36.48k

W14x26 = 13.9x.255x50=177k > 36.48k

Column Selection:

VTotal = w x L  =   = (11.04/2) (13.2)  / 2  =  72.86k

Each column supports half the load =  72.86k /2 =  36.43k

Column Slenderness factor K = 1.5

Column height = KL = 1.5 x 10 = 15

HSS4x ¼”    Fy = 46 ksi