Fax 646-4176

April 11, 2005

Ms. Denise Jobe

St Tammany Parish

21490 Koop Drive

Mandeville, LA  70471

RE:
Permit No. K05-144

Pool Installation

Mike & Mary Seaner/#140 Carmel

Mandeville, La./St. Tammany Parish

Dear Ms. Jobe,

ABC Electric asked us to inspect the electrical work that they had completed for the pool installation.  They said that after the electrical work was completed, Paradise Pools poured the concrete deck around the pool without the necessary electrical inspection from your office.

We visited the site and determined with an ohmmeter that all grounding is complete and meets the requirements of the National Electrical Code for grounding.

It is my professional opinion that the electrical work was installed to meet the above code, to the best of my knowledge and belief.

To the extent of compliance with the laws regarding the electrical work of this structure, I certify and accept professional responsibility that it meets the grounding provisions of the National Electrical Code and all other provisions and associated laws governing this work.

This report does not cover any other aspects of the structure such as plumbing, structural, gas, mechanical, egress, general arrangement, etc.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

