[image: image1.jpg]DAMMON ENGINEERING, INC.

dammonengineering.com

ARCHITECTS ENGINEERS
CONSULTING DESIGN STUDIES EXPERT WITNESS
1095 Florida Ave. P.O. Box 2830 985-649-5832
Slidell, LA 70458 Slidell. LA 70459 FAX 985-641-3950

December 10, 2007

O’Brien Flooring, Inc. / Northshore Flooring Distributors, Inc.
189 Commercial Square

Slidell, LA 70461

Attn: Frank & Mike O’Brien

Via fax: 726-5191

Re: New Office / Warehouse
Dear Frank & Mike,

Today I researched the code regarding putting in a partial sprinkler system,
for just the warehouse area, as we discussed over the phone on Friday. The
code will allow this, but I do not see any advantage, because you will still
have to separate the warehouse from the office area with fire wall
construction, to keep you under the 12,000 sq. ft. fire area limit. Once your
“fire area” is over 12,000 s.f., you must sprinkle 100% of the building. I
don’t think you want to pay for sprinklering 70% of the building and having
to do the fire wall construction too.

So we are back to two choices:

1. No sprinkler system - éémplete fire wall construction required
between office and warehouse as per my letter to you of December
6".

2. Sprinkler system for 100% of the building- non-fire rated construction
allowed.

We need a decision on this, and the soil and site data to finish the plans.
We can go the Fire Marshall for plan review without the soil boring data.

Sincerely, 3
Robert Wiltse
Architect

Dammon Engineering, Inc.




