[image: image1.jpg]IDAMMON

ENGINEERING | NLC.

J  Archiltectls & Engineers




554 Old Spanish Trail
Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net


August 15, 2013
Mr. Anouar Ait Iddir

1300 Perdido Street

City Hall-Room 7E06

New Orleans, LA  70112

RE:
15140 Intracoastal Dr.


Permit No. 13-08892-RNVN

Mr. Iddir

Please note the following responses to your letter dated July 19, 2013, copy attached.

Electrical:

2) You only submitted 1 copy of stamped set of plan.  

Please find 2 sets of stamped Electrical Drawings

3)  Sheet E1, Please clearly mark all the circuit designations for all light fixtures and receptacles.

E1 has been revised to reflect current circuit designations.

4)  Sheet E1, please provide a detail drawing of the grounding system of the 75 kVA transformer as per NEC 2011 Art. 250.

E1 has been revised to include a detail of the grounding system for the 75kVA transformer.
5)  Sheet E1, please label the specification of the feeder going from Fused Disconnect to MDP.

E1 has been revised to include the specification for the feeder.
6)  Sheet E1, all panel schedules shall provide details of available short circuit currents at service and secondary panels.

Please find attached a calculation for Available Fault Current.

Sincerely,
David Dammon, VP

Dammon Engineering, Inc.
Bill Kingsmill’s contact information is as follows:
William Kingsmill (kingsmillprop@bellsouth.net)
Cell: (504) 528 3838
1200 Business Highway 190, Suite 13
Covington, LA 70433
 
Lawrence Wm. Haik, Sr
Republic Commercial Properties, LLC                
1539 Royal Palm Dr.
Slidell, LA 70458
(985) 960-7033
 
