March 9, 2005

Mr. John Whitaker

Office of State Fire Marshal

8181 Independence Boulevard

Baton Rouge, Louisiana 70806

RE:
P0280462

Jim Goff Warehouse

Ben Thomas Rd.

Slidell, La. 70458

Dear Mr. Whitaker,
On 8-30-04 you approved a set of plans for an office warehouse located on Ben Thomas Road.  The building is a total of 6,000 square feet; part of that is an office of 1,950 square feet.  Above the office is a mezzanine with two exits.  We have rated the wall (1 hour) separating the office from the warehouse up to the mezzanine floor.  You noted on the drawing that the mezzanine floor also shall be rated for 1 hour.
We would like to offer, as an equivalent, that we add four smoke detectors above the mezzanine.  We feel that this is sufficient to meet these needs.  Please see the attached sketch.  We would appreciate your approval in this matter.

Please call me with any questions that you may have.

Thank you,

Chuck Dammon

VP/Project Manager

