Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

October 31, 2007

Ms. Christi Burkart, CPM

Senior Property Manager

Equity Office Properties

RE:
Response to AS-BUILT Review 

21st, 22nd, 23rd and 25th Floors

Peoples Health Network
Dear Ms. Burkart,

The following responses are provided to the comments made during review of plans of the As-Built up-fit renovations on the 21st, 22nd, 23rd and 25th Floors by Craig Clement.

Sheet E-1 for the 21st floor there is a note that reads “outlets have no power”  


The note was inadvertently left on the drawing.  A revised copy of the 21st floor E-1 is provided.

Sheet E-1 for the 23rd floor transformers were added and installed in a closet.  There does not appear to be any information for how the heat rejection is being accommodated.  Also there is no riser or single line diagram indicating the feeder connections for the new transformers and panels.



The closet housing the transformers is vented into the HVAC return air plenum ceiling.  This will be noted on the final Mechanical plan submitted after the balancing is complete.  The feeder connection single line diagram has been added to the As-Built drawings.  Please find 23rd floor E-3 As-Built drawing attached.

There are no fire alarm devices, power supplies or appliances indicated.  


A copy of the As-Built alarm device drawings and packages is being provided.  

After the HVAC balancing has been completed and added to the list of electronic files a new CD will be provided as well as complete set(s) of hard copies. 


Sincerely,

David Dammon

Project Manager

