[image: image1.jpg]


554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com
[image: image2.png]



January 11, 2016
September 13, 2016
Mr. Brandon Comeaux E.I.,
Region 1 Engineer Intern

OPH – District 1
RE:
Edenbourne Courts Apartments


3312 Edenbourne Ave.

Metairie, Louisiana 70002
Mr. Comeaux,

In response to your review letter dated September 1, 2016 regarding concerns about the Edenbourne Courts Apartments pool plans, the following is provided:

1.  Please clarify that the pools surface skimmer flow rates are within the manufacturers specifications.  Model Aquatic Health code 2nd edition 4.7.1.5.3, “The flow rate for the SKIMMERS shall comply with the manufacturer data plates or NSF/ANSI 50 including Annex K.”.

   Response: Although the CDC Model Aquatic Health Code (MAHC) has not been adopted by the State of Louisiana for use in designing nor reviewing of pool plans, the CDC code states:

5.7.1.1.3 Gutter / Skimmer Pools For gutter or SKIMMER POOLS with main drains, the required recirculation flow shall be as follows during normal operation: 

1) At least 80% of the flow through the perimeter overflow system, and 
2) No greater than 20% through the main drain. .


This pool has been designed to operate with two skimmers recirculating 85% of the pool total flow and the main drain recirculating 15% total flow.  85% of 106 GPM = 90.1 divided by two skimmers = 45.1 GPM.  The skimmers that are specified can handle up to 50 GPM under normal operating conditions and can safely handle 55 GPM under other than normal conditions.  See attached revised Pipe Schedule.  
If you have any questions, or require additional information, please feel free to call.

Sincerely,

[image: image3.jpg]‘,\u\umm,





David Dammon, President



  9/13/2016
Dammon Engineering, Inc.

