RETURN HEAD

Pressure Loss (psi):  3.47   Head Loss (ft):  8

Line Number:

Date:  7/19/2016

Nominal Pipe Size:  2

Pipe Schedule:  SCH 40

Flow Rate (gpm):  50

Viscosity (cP):  1

Specific Gravity (water=1):  1

Temperature (F):  70

Pipe Roughness (ft):  0.000016

Actual Pipe ID (in.):  2.067

Fluid Velocity (ft/sec):  4.78

Reynolds Number:  76502

Flow Region:  Turbulent

Friction Factor:  0.019

Overall K:  22.59

Piping Length (ft):   200                                                 8.0

10  -  90 degree elbows                                                      1.4

3 tees                                                                                          1.2

chlorinator                                                                                0.5

sand filter                                                                                   5.0

3 ball valves                                                                               0.4

flow meter                                                                                  2.0

3 directional eyeballs                                                             6.3

total                                                                                             24.8

------------------------------------------------------------------------------------------------------

SUCTION HEAD

3 ball valves                                                                               0.4

2 skimmers                                                                                    4.0

2main drains                                                                                 5

3 tees                                                                                                1.2

Piping Length (ft):   200                                                           8.0

Total                                                                                              18.6

-------------------------------------------------------------------------------------------------------

Total Head Loss     18.6   +    24.8         =                           43.4